## Structural
Date
16-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HANDZ CLOTHING BD LTD., 433/1,Nanduain,Masterbari,Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2025-12-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Lack of lateral stability (Main Production Shed). | The building engineer is required to check the lateral stability of the structure as part of the DEA and propose a remediation plan if required. | Facility will appoint a DEA firm and submit DEA. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 2 | Lack of lateral stability (Main Production Shed). | Verify in-situ steel strength. | Facility will appoint a qulified structural engineer to conduct in situ steel strenth testing and submit the verified test report to RSC within the agreed timeline | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 3 | Lack of lateral stability (Main Production Shed). | Carryout suggested remedial works. | Based on DEA approval remediation will be performed. | Jul 5 2026 |  | within 6 months | In Progress
Initial Inspection |  | 4 | Lack of a geotechnical investigation report (Main Production Shed). | A geotechnical engineer must be engaged to prepare a geotechnical investigation report to determine the soil bearing capacity. | Facility will Engauge a geotechnical engineer to investigate soil bearing capacity. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 5 | Lack of a geotechnical investigation report (Main Production Shed). | Based on geotechnical data, check the foundation adequacy as part of DEA. | The report will be consider to DEA | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 6 | Faulty connection in vertical bracing (Main Production Shed). | The building engineer is required to check the load path and connection adequacy and propose a remediation plan. | Facility Load maanger will check and calcuate the connection and will take remediation based on result. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 7 | Possibility of construction of a new mezzanine floor (Main Production Shed). | Any addition to the new existing structure not shown in the permit drawing, the building engineer is required to take a fresh permit from the local authority and carry out a Detailed Engineering Assessment (DEA) in compliance with BNBC 2020. | Facility will consider the technical guideline before construct the mezzanine floor. | Jul 5 2026 |  | within 6 months | In Progress
Initial Inspection |  | 8 | Discrepancy and missing information in the provided drawing (Main Production Shed). | The building engineer is required to update the as-built drawing. | Facility engineer will update as built drawing | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 9 | Corrosion on steel members (Main Production Shed). | The building engineer is required to remove the corrosion and provide rust proof paint on steel members. | Facility will remove the corrosion and paint as requored. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 10 | Loose cable bracing (Main Production Shed) | Tighten all loose bracings. | Facility will Tight all loose bracings. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 11 | Non-structural elements found unanchored/braced (Main Production Shed). | The building engineer is required to anchor/brace all nonstructural elements within the factory. | Facility management will anchor all nonstructural elements | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 12 | Lack of design documents. (Generator & Substation Building) | The building engineer is required to prepare design documents (including design reports, material test reports, and live load plan) in compliance with section 1.9.1 (part 6, BNBC). | Facility engineer will prepare and updatte all design reports, according to BNBC section.. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 13 | Lack of design documents. (Generator & Substation Building) | Produce accurate as-built drawings. | Facility engineer will prepare as built drawing and submit it to RSC. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 14 | Lack of design documents. (Generator & Substation Building) | Carry out the suggested remedial works. | Based on as built remediation will be performed. | Jul 5 2026 |  | within 6 months | In Progress
Initial Inspection |  | 15 | Dampness on the beam, column, and brick wall. (Generator & Substation Building) | Building engineer to prepare an investigation report, seal the source of water, and repair the dampness as per the investigation report. | Facility building engineer will investigate the source of lickage water and will take prevention for damage. And exsiting damaged will be repared. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 16 | Non-structural elements found unbraced/not anchored. (Generator & Substation Building) | The factory is required to brace/anchor all non-structural elements. | Facility will brace/anchor all non-structural elements | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 17 | Exposed rebar on the roof level. (Generator & Substation Building) | The building engineer is required to provide anti-corrosive coating on the exposed rebar. | Facility building engineer will coated anti-corrosive coating on the exposed rebar. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 18 | Apparently non-engineered connection/Shed. (Medical & Childcare Shed) | The building engineer is required to check the connection of the steel roof for the uplift pressure of wind as part of the Engineering Assessment (EA). | Facility will engage aqualified structural engineer to check the steel roof connection for wind uplift pressure as per BNBC. Necessary strengthening will be carried out if required. The assessment report and engineer`s certification will be submitted to RSC. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 19 | Apparently non-engineered connection/Shed. (Medical & Childcare Shed) | The building engineer is required to separate the connection and provide new columns for structures. Otherwise, analyze these buildings as a single structure. | Facility will appoint a structural engineer to assess the requirement of structural separation. If requirded, separation and new column will be provided; otherwise , the building will be analyzed as a single structure. Report and certification will be submitted to RSC. | Jul 5 2026 |  | within 6 months | In Progress
Initial Inspection |  | 20 | Apparently non-engineered connection/Shed. (Medical & Childcare Shed) | Complete implementation of remedial works if required. | Facility will complele the implementation of remedial works as per the structural engineer`s recommendation, if required, and submit the completion report with certification to RSC. | Jul 5 2026 |  | within 6 months | In Progress
Initial Inspection |  | 21 | Discrepancy in the as-built drawing (Medical & Childcare Shed) | The building engineer is required to survey the whole structure and prepare an accurate as-built drawing. | Facility building engineerwill survey the whole structure and prepare an accurate as-built drawing and submit to review. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 22 | Exposed rebar on the roof level. (Security Room) | The building engineer is required to provide anti-corrosive coating on the exposed rebar. | Facility building engineewill coat anti-corrosive coating on the exposed rebar. | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 23 | Lack of anchorage between the steel member and the brick wall (Cartoon Godown Shed). | Prepare the proper connection details of the steel rafter to the Brick wall connection as part of the safety check report and submit it to RSC for review. | Facility will perfom a DEA considering e proper connection details of the steel rafter to the Brick wall connection as part of the safety check and it will be submit to RSC for review | Mar 10 2026 |  | within 6 weeks | In Progress
Initial Inspection |  | 24 | Lack of anchorage between the steel member and the brick wall (Cartoon Godown Shed). | Implement remediation work, as per the accepted drawing from RSC. | Remediation will be perfom as per the accepted drawing from RSC. | Jul 5 2026 |  | within 6 months | In Progress

## Fire
Date
16-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HANDZ CLOTHING BD LTD., 433/1,Nanduain,Masterbari,Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2025-12-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The egress path along means of egress has interrupted by obstruction/storage/process Location(s): Main Production Shed. | Keep egress paths clear of storage/obstruction in accordance with section 6.3.9 of RSC Technical Guidelines (Standard)¹ V1.0.Means of egress shall be maintained continuously free and clear of all obstructions or impediments to full instant use in the case of fire or other emergency. No furnishings, decorations, or other objects shall obstruct exits and access to exits. Nothing shall obstruct or impede visibility to exits. | 1. All fabric rolls, process materials, and temporary storage identified during the inspection have been removed from the yellow-marked egress paths. 2. Redesigning the layout to create dedicated "In-Process Workstations" so materials do not overflow into the egress path. 3. P20Also, a specialized fire safety training given for all operators regarding the life-safety risks of blocked exits. | Jan 6 2026 | Remediation will be verified during the next inspection schedule. | Immediately | Pending Verification
Initial Inspection |  | 2 | Doors along means of egress are provided with non-compliant locking devices. Location: South side of the production Shed & all other structures. | Remove locking devices from all egress devices in accordance with section 6.8.2 of RSC Technical Guidelines (Standard)¹ V1.0 | 1. All non-compliant locking devices, including padlocks and manual sliding bolts, have been removed from the south side of the production shed. 2. Doors are currently maintained in an unlocked position during all working hours to ensure immediate egress. 3. We are in the process of procuring and installing "Single Action Exit P21Hardware" (e.g., Panic Bars) that allows the door to open from the inside without the use of a key or any special effort, as per RSC Technical Guidelines Section 6.8.2. | Jan 6 2026 | Remediation will be verified during the next inspection schedule. | Immediately | Pending Verification
Initial Inspection |  | 3 | Posted Fire evacuation maps are not updated as per site conditions. Location(s): Production Shed & other all structures. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | Facility will update All evacuation plan according to existing Machin lay out. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 4 | Stair clear width was found less than 60 in. Location(s): Generator & Substation Building Available Width: 44inch | Stairs shall have a minimum clear width of 60 in. in for all industrial occupancies as per RSC Technical Guideline (Standard) section of 6.5.6 | 1. Stair width narrow (Location : Existing worker dinning ) in the landing of stair there have sub -Station Room`s opening exit which obstacle to the stair. Thats why we facility management wants to relocate the dining area with confirm of RSC safty management. 2. stair width narrow location of main building . Facility will remediate and rearrange the stair widths to 60-inch in accordance with the RSC Technical Guide line Section 6.5.6. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 5 | Illuminated Directional signs are not provided where direction of the path of travel to an exit has changed. Location(s): Main Production Shed. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | Facility management will check Illumination of directional signs and will be installed in accordance with passage and exist direction. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 6 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location(s): All structures | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. Illumination on means of egress shall meet in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 10.12.2. | Facility will Test the emergency lighting system on each floor and based on result will installed additional emergency fixtures to meet 10 lux at the floor level and exit stairs and exit discharge paths and 2.5 lux minimum. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 7 | The maximum travel distance exceeds 45 m which does not meet the requirements of Section 6.13 of RSC Technical Guidelines (Standard). Location: GF, Main production Shed.Occupancy/Process: Sewing section | Reconfigure the egress arrangement to meet 6.13 of RSC Technical Guidelines (Standard). Or, Provide additional exits so that the travel distance shall not exceed the maximum allowable limit. | Facility will arrange a additional exit to meet the maximum travel distance within 45 m. based on DEA. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 8 | Doors are swing out over stairs. Location: Generator & Substation Building | A landing shall be provided on both sides of doors used in the means of egress to facilitate uninterrupted egress of occupants. Door shall not swing out over stairs. Landings with same width as the stair clear width shall be provided at each level and at intermediate landings. | 1. Landings: Constructing permanent landings on both sides of all egress doors where they are currently missing. 2. Door Swing Correction: Re-engineering door frames to ensure they do not swing out over staircases, maintaining the full clear width of each intermediate landing as required by safety standards." | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Mon | In Progress
Initial Inspection |  | 9 | The exterior exit stair is not separated from the building interior. Location: Location: Generator & Substation Building | Nonrated walls or unprotected openings enclose the exterior of the stairway and the walls or openings are exposed by other parts of the building at an angle of less than 180 degrees (3.14 rad), the building exterior walls within 3050 mm (10 ft) horizontally of a nonrated wall or unprotected opening shall have a fire-resistance rating of not less than 1 hr. in accordance with section 6.3.1.3 of RSC Technical Guidelines (Standard)¹ V1.0 | Facility will separate the Exterior exit stair from the building interior in accordance with standards. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 10 | Exit signage not illuminated during testing (burned out, broken, etc.). Location(s): All structures | Regularly inspect all exit signage/directional signage as per RSC Technical Guidelines (Standard)¹ V1.0. and replace/install lights as needed to illuminate signs | Facility already inspected & tested is conducted, few signs found low quality. Will change the exit signage and confirm the required illumination. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 11 | Handrails are not provided on both sides of Final exit discharge stairs. Location(s): South side of Main Production Shed.Non-Compliance: Handrail are not provided both side. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.). Open guards shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.). Handrail shall construct in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.12. | Facility will arrange a hand rail with 34 " height | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 12 | Building does not have occupant load signs at required locations on floor.Location(s): All Structures | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4 | Facility will post Occupant load capacity board. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 13 | Exit sign not provided at exit.Location(s): Main Production Shed & Cartoon Godown Shed. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious.Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11. | Facility will install Exit sign with battery backup will posted at mentioned areas and location. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 14 | Manual on-off switch is provided for exit signage units. Location(s): Main Production Shed. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off | Facility Is disconnect all manual switch from the exit signages. Pictures have been added to pictorial documents. This work is ongoing and will require another month to complite. | Feb 15 2026 | Remediation will be verified during the next inspection schedule. | Within 1 Month | Pending Verification
Initial Inspection |  | 15 | Rooms used for storage of combustible materials are not separated from the surrounding occupancy(Production) Location: GF, Main Production Shed. Non-compliance reason: Due to unprotected opening | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction in accordance with section 3.4.2.1.5 of RSC Technical Guideline (Standard). Keep proper datasheet & certifications for installed fire doors & accessories on-site for verification. | Facility will installed a fire door and will separate the fire hazards and occupancies. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 16 | Storages were found underneath the cutting tables. Location(s): Main Production Shed | Storage underneath the cutting tables shall be kept clear of combustibles at all time, except as provided for miscellaneous storage in accordance with 3.4.2.1.6 or ,Where an automatic sprinkler system is installed sprinklers are required to be installed beneath cutting tables greater than 4 ft in width that are used for storage of combustibles | Facility removed the storage to kept clear of combustibles. | Apr 15 2026 | Remediation will be verified during the next inspection schedule. | Within 3 Months | Pending Verification
Initial Inspection |  | 17 | The day-care room does not separated from other occupancy (Dining area) Location: Medical & Childcare Shed. | Separate the day-care from other occupancy ac per Table 3.2.1 (BNBC 2006) | Facility Will separate the day care center from other occupancy as per BNBC . | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 18 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location: GF, Main Production Shed | Provide defined storage areas and limit the storage arrangement as follows: Maximum height of 2.45 m and maximum area of 23 m² and is separated by a minimum 3.0 m (10ft) from other storage areas and they do not exceed 10 percent of the building area of the story in which they occur. or,If sprinkler protected, Maximum height 12 ft (3.66 m) and maximum area of 1000 ft² (93 m²) and separated by a at least 25 ft (7.62 m) and does not constitute more than 10 percent of the building area or 4000 ft² (372 m²) of the sprinklered area, whichever is greater. or,Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | facility Will maintain the mentioned guideline for process storage. | Apr 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 19 | Transformer is not properly separated from exit stairs by fire rated construction due to unprotected opening Location: GF, Generator & Substation Building.Non-compliance reason: Unprotected opening. | Oil filled transformer shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wall in between. Seal all penetrations and openings (door, window etc.) should be protected by 1.5-hr fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Oil filled transformers shall not be housed above ground levelOr, Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Transformer room separation shall meet section 3.4.2.1.4 of RSC Technical Guideline (Standard) | Facility will construct a fire separation at transformer area to address the unprotected opening. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 20 | Single exit is provided at the dining/canteen area on two storied Generator & Substation Building.Location: First floor of the Generator & Substation building. | Assemblies of Occupancy E3, E4 and E5 shall have at least two means of exits leading directly to the street or leading to a corridor or open space having access to exits in two independent and different directions. (part-4, section-3.21.3, BNBC-2006). The required number of exits for the entire assembly arrangement shall lead directly to safe dischargepath without passing through any other occupancies | Facility will arrange 2nd exit for dinning and canteen area. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 21 | The required fire separation distance for the (Main Production Shed) does not comply with the requirements of BNBC 2020Location: North ,South side & east side of the Main Production Shed. | The exterior walls shall have a fire resistance and opening protection as specified in BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3 | Facility will sealed the opening and confirm the fire separation. | Jul 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 6 Months | In Progress
Initial Inspection |  | 22 | The required fire separation distance for the (Cartoon Godown Shed) does not comply with the requirements of BNBC 2020Location: North ,South side & West side of the Cartoon Godown Shed | The exterior walls shall have a fire resistance and opening protection as specified in BNBC 2020 Part 3 Table 3.2.2 & 3.2.3 and BNBC 2020 Part 3 Section 2.4.1.3 | Facility will sealed the opening and confirm the fire separation. | Jul 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 6 Months | In Progress
Initial Inspection |  | 23 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards.Location(s): All Structures | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72 to meet section 5.7.3 of RSC Technical Guideline (Standard) Submit the proposed fire alarm system design to RSC for review. Once the design is reviewed, install and modify the fire detection and alarm system throughout the building in accordance with review comment, RSC/ RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | Facility will appoint a RSC approved safety consultant for probation of CFDS, Design will be submitted 30 April 2026. Based on approval procurement and installation will be performed. | Jul 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Design within 2 Month and modification/ installation with 4 Months | In Progress
Initial Inspection |  | 24 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72and RSC Technical Guidelines (Standard)¹ V1.0.s. | Facility will perform testing & maintenance as per NFPA 72 after installation. | Aug 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. It is an integrated part of FADS. | Within 1 Month after installation | In Progress
Initial Inspection |  | 25 | The travel distance between portable fire extinguishers were found to be more than 30 m (100 ft). Location(s): Main Production Shed. | Portable fire extinguishers shall be installed throughout all new, interim, and existing facilities in accordance with BNBC 2006 and NFPA 10. Extinguishers shall be placed so that maximum travel distance to the nearest unit shall not exceed 30 m (100 ft). | Facility will re-arrange the portable fire extinguishers in accordance with travel distance 30 m. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 26 | The required no smoking signs are not present in the factory | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. Smoking sign shall post in accordance with section 13.5 of RSC Technical Guideline (Standard) | Facility will posted no smoking signage for all required area. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month. | In Progress
Initial Inspection |  | 27 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Inspection, testing and maintenance will be performed in accordance with NFPA 72. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 28 | Fire drills are not conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. | Fire drills shall be conducted according to section 13.2 of RSC Technical Guidelines (Standard)¹ V1.0. Fire drills shall be conducted on a monthly basis as outlined in BNBC 2020 Part 4 Appendix A. | Facility will conduct fire drill and maintain document. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 29 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with the RSC Technical Guidelines (Standard)¹ V1.0.. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC Technical Guidelines (Standard)¹ V1.0.. Keep written records on-site. | Inspection, testing and maintenance will be performed in accordance with RSC Standards. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 30 | Written housekeeping policy was not found, which is required as per RSC Technical Guideline (Standard) section 13.6. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delay and rescheduling. As a general rule the maximum tolerable deposit thickness for loose fluffy lint is 13 mm (½ in.) over a maximum of 46.5 m2 (500 ft2). Limit dense deposits to 6 mm (¼ in.) and oil saturated deposits to 3.2 mm (⅛ in.). | Facility will formed a housekeeping policy for ensuring better fire safety and cleanliness. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress
Initial Inspection |  | 31 | The Building approval from appropriate authority are not available at siteLocation: Security Room & Cartoon Godown Shed | Get all the required licenses and permits from the proper issuing authority and keep it at site. | Factory will collect the building approval from the concern authority. | Apr 30 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 3 Months | In Progress
Initial Inspection |  | 32 | Hot-work permit program is not established yet, although it is required. However, hot-work is not going on in the factory right now | Develop a hot-work permit program. The program must comply with the requirements of NFPA 51B. In general, this program should address the process of request and approval of authorities, necessary checks prior approval, standby fire watch and fire fighting equipment, sounding of alarm procedure, duration and expiry of permit and re-approval procedures, etc. | Facility management set a Hot work permit according to policy. This work is ongoing and will require another month to complite. | Feb 15 2026 | The remediation work shall be done following provided remediation guideline and applicable standard within the committed timeline. | Within 1 Month | In Progress

## Electrical
Date
16-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HANDZ CLOTHING BD LTD., 433/1,Nanduain,Masterbari,Gazipur., Gazipur, Dhaka
Date of Inspection |  | 2025-12-10
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. | Facility will prepared a As-built Electrical Single Line Diagram (SLD) and will submit to RSC for review. As approval installation will perform | Jul 30 2026 |  | 6 Months | In Progress
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (according to BNBC). | For factory buildings with a Risk Index of 40 or higher, a comprehensive Lightning Protection System (LPS) required to be designed as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | Facility will prepared a LPS design and will submit to RSC for review. As approval installation will perform | Jul 30 2026 |  | 6 Months | In Progress
Initial Inspection |  | 3 | Electric safety training program is not initiated by qualified electrical personnel. | Electrical safety training and awareness programs for electrical personnel must be conducted regularly by qualified personnel and documented. This periodic task is crucial for continuously improving overall electrical safety for factory staff. | Facility will conduct safety training for electrician. | Feb 5 2026 |  | 1 Month | In Progress
Initial Inspection |  | 4 | No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. | Facility will ensure PPE for electrician and awareness will also given. LOTO policy will prepared and equipment will also purchased. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 5 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | Electrical maintenance program shall be developed to include regular inspections and testing of electrical systems, focusing on preventive and proactive measures. | Facility will prepared a preventive maintenance plan and follow accordingly. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 6 | Transformer oil test (dielectric strength test) report is unavailable. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, DPDC, or any other designated govt. authority. This ensures adherence to an unaltered, verifiable, standardized format, thereby maintaining the integrity and reliability of the transformer's insulation system. | Facility will test the transformer oil on periodic basis. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 7 | Earth pit resistance record is not available. | All earthing systems must be tested for resistance on a dry day at least once every two years. Records of each earthing test and its results must be available for inspection when required. | Facility will perform earthing test for all point and report will be kept for review. And minimum level will be ensured. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 8 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. | Facility will collect Insulation resistance test report and perform periodical check every 2 years. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 9 | Thermography scanning report is not available. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. | Facility conduct Thermography survey and find the hit source and according to report will remediate the temperature. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 10 | Earth resistance is not satisfactory. | The earth resistance of electrical systems and equipment earthing shall be maintained at a maximum of 1 ohm. | Facility will installed earth resistance system for electrical safety and ensure Ω level. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 2 Months | In Progress
Initial Inspection |  | 11 | Inadequate working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (Transformer). | A solid-type working separation, preferably a brick wall, must be established between LT (Low Tension) and HT (High Tension) areas. Additionally, adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. | Facility will construct a separation with clear of maintenance | May 5 2026 |  | 4 Months | In Progress
Initial Inspection |  | 12 | Inadequate working space around transformer for performing maintenance work. | Adequate working clearance and proper ventilation must be maintained in accordance with RSC technical guidelines. This ensures the safe operation of electrical systems, prevents cross-contamination between LT and HT sections, and enhances overall safety and operational efficiency. Access needs to be restricted to qualified personnel wearing appropriate PPE (Personal Protective Equipment). | Facility will ensure working clearance path and ventilation for LT and HT | May 31 2026 |  | 4 Months | In Progress
Initial Inspection |  | 13 | Transformer body earthing (equipment earthing) cable is inadequate. | The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. | Factory will install required earth pith according to code and SLD. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 14 | Maintenance movement is obstacle due to uneven height of cable duct/tray/ trench in utility area (generator). | The workspace surrounding the transformer, generator, or any other electrical installations must be level and uniform in height. This ensures safe and efficient access for maintenance and operational activities while minimizing potential trip hazards, thereby enhancing overall safety and productivity. | Facility will re arrange the utility for maintenance clearance. | Apr 30 2026 |  | 2 Months | In Progress
Initial Inspection |  | 15 | Lead acid battery terminals are filled with rust and left open. | Lead-acid battery terminals must be covered or capped, and any rust must be thoroughly cleaned to ensure safe and efficient operation. | Facility will covered battery terminal | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 16 | Generator body earthing (equipment earthing) cable is inadequate. | Ensure that the generator is equipped with at least two separate earth pits. The size of the earth cable shall be determined according to BNBC or the Adiabatic method. The number of earth pits shall be calculated based on acknowledged standards to ensure effectiveness. | Facility will installed generator body earthing separately and will ensure minimum Ω. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 17 | Generator terminal box left open to allow cable entry. | Generator terminal box must have a base plate installed, and cables entering the terminal box must be securely fixed with cable glands. | Facility will install Generator terminal box with a base plate , and cables entering the terminal box must be securely fixed with cable glands. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 18 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instructions must be posted near all electrical installations (such as LT panels, MDBs, FDBs, DBs, and SDBs) in a clearly visible location. | Facility posted CPR instructions visible all hazard areas. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 19 | Danger signs are not available on each electrical panel/board. | Danger signs must be displayed on each electrical panel or board, clearly indicating the proper voltage information to ensure safety and awareness of electrical hazards. | Facility will post Danger signs on each electrical panel or board with clearly indicating the proper voltage information . This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 20 | Distribution boards have no clear identification markings. | Clearly mark all distribution boards, switchboards, sub-main boards, and switches for identification. | Facility will Clearly marked all distribution boards, switchboards, sub-main boards, and switches for identification. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 21 | Power cables are not identified properly. | All power cables must be clearly and distinctly marked in accordance with the Single Line Diagram (SLD) to ensure proper identification, safe handling, and efficient operation. | Facility will marked the cable according to SLD. For safe handling.. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 22 | Panel doors are not connected with earth. | All metal components within the electrical system must be securely connected to the earth. This earthing is essential to mitigate the risk of electrical shock or electrocution by providing a safe path for fault currents to dissipate. | Facility will install earthing connection for All metal components within the electrical system. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 23 | Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board or panel must be sealed to prevent the ingress of fluffs and dust. Adequate ventilation must also be ensured to maintain optimal operating temperatures. Cable glands should be used where required to secure cables and maintain the integrity of the seal. | Facility will sealed Each electrical DB to prevent the ingress of fluffs and dust. Adequate ventilation will be ensured . Cable glands will be installed . | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 24 | Circuit breaker has no capacity information. | Each circuit breaker must be clearly labeled with its capacity information. | Facility will labeled Each circuit breaker with capacity information. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 25 | Protective device is not installed/ adjusted per load demand. | Protective devices must be installed or adjusted according to the connected load current. If adjustment is not feasible, replacement is necessary. Each motor load exceeding 376W requires separate protection, adhering to nameplate data for selecting the appropriate protective device. | Facility will installed or adjusted Protective devices to the connected load current. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 26 | Phase barrier/separators are missing in circuit breaker. | Phases must be separated by insulators made from non-flammable rubber-type materials to prevent electrical short circuits and enhance safety. | Facility will separated Phases by insulators made from non-flammable rubber-type materials to prevent electrical short circuits and enhance safety. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 27 | Multiple cables from different electrical consumers are terminated at busbars. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | Facility will install a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 28 | Cable connected to busbar/circuit breakers terminal without cable lug. | Each electrical circuit must be terminated at single busbar/circuit breakers terminal using cable proper sized cable lug (where applicable). | Facility will install single busbar/circuit breakers terminal using cable proper sized cable lug (where applicable). | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 29 | Nut-bolt, bus-bar & washer are rusted in the sub/distribution board. | Rusted nut-bolt, bus-bar & washer must be replaced with new one. | Facility will replace all Rusted nut-bolt, bus-bar & washer | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 30 | Burnt sign visible at circuit breaker/ cable lug. | Check the connections and circuit breaker to identify the cause of the burning. If necessary, replace the burned breaker. Assign an engineer to take the appropriate action based on the problem identified. | Facility will change all burned brakers from the DB and panel. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 31 | Power cables entering or exiting from distribution board/panel are not fixed. | Power cables entering or exiting the distribution board/panel must be fixed through the base or top plate with proper size cable gland (metal or PVC) of the correct size. | Facility will repair and fix top plate with proper size cable gland (metal or PVC) of the correct size. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 32 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. | Facility will ensure Raber mat for electrical installation minimum 3 mm thickness and 1 m width. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 33 | Unterminated wire is kept inside the floor. | All unterminated power cables must be expeditiously removed. | Facility will remove unterminated power cables. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 34 | Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. | Facility will ensure cable joint through porcelain/PVC connectors with PIB tape. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 35 | Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Ensure that any heat source (or steam line) is kept at least 0.9 meters away from any electrical installation. If unavoidable, the heat source must be covered with a suitable insulator. | Facility will ensure the heat source is kept at least 0.9 meters away from any electrical installation. This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 36 | Uncovered type cable used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Facility will waring the storage area, by GI pipe/solid metal duct or concealed wiring system. | Apr 30 2026 |  | 3 Months | In Progress
Initial Inspection |  | 37 | Earth lead cable/Earth Continuity Conductor size is not available for distribution circuits. | Earth lead cable/ Earth Continuity Conductor (ECC) shall be determined according to BNBC or Adiabatic method (considering CB's response time, fault current & type of earth conductor other factors). | Facility will install ECC as BNBC standards. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 38 | Combustible/flammable materials are attached with electrical panel board/BBT/cable channel/duct. | All flammable and combustible materials, including water bottles and other items, must be cleared from electrical cable channels, ducts, and BBTs. Separate storage arrangements for these materials should be implemented. | Facility will remove all flammable and combustible materials, including water bottles and other items close to electrical cable channels, ducts, and BBTs. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 40 | Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine, accessible to users/operators, must be equipped with an earth connection. Cable selection should be based on the protective device's response and the power demand of the circuit. | Facility will install earth connection for all manual operated machines . This work is ongoing and will require another month to complite. | Feb 15 2026 |  | 1 Month | In Progress
Initial Inspection |  | 41 | Exhaust fan body and fan blade enclosure are not equipped with earth connection. | Exhaust fan frame and its enclosure in the production area/s shall be connected to earth. | Facility install Exhaust fans earthing connection. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 42 | Uninsulated electrical tools are used by maintenance personnel in the factory. | All electrical tools must be properly insulated for maintenance purposes, and these insulations should be periodically inspected. | Facility will calibrated all electrical tools periodically. | Mar 31 2026 |  | 2 Months | In Progress
Initial Inspection |  | 43 | HT cable earth linkage current collector is not connected. | Connect the HT cable earth linkage/current collector as per standards and ensure proper bonding to the earthing system. Verify continuity after completion. | Facility will install earth connection for HT panel. | Mar 31 2026 |  | 2 Months | In Progress

## Boiler
Date
16-Mar-2026 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed | Yes