## Structural
Date
01-Sep-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HR TEXTILE/FASHION KNIT, 4 Karnapara, Savar, Dhaka,, Dhaka
Date of Inspection |  | 2014-05-11
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Columns appear to be stressed to a high level and require immediate review. | Factory Engineer to review design, loads and column stresses in all columns. Particular check to be completed for columns which are smaller than shown on the drawings –see highlighted area . | Corrected | Nov 30 2014 | On 28/06/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On verification period factory management didn’t shown any DEA copy because in factory level no DEA report copy. On 18/08/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: This issue was covered in DEA. Factory has done DEA which was accepted by ACCORD on 26/01/2017. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 30-May-2017: DEA has been accepted from ACCORD. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 03-12-2017: Factory has already reviewed the design based on as built condition which was got acceptance from ACCORD. On 31/12/2017: Found corrected from previous follow up inspection. On 16/07/2018: Found corrected from previous follow inspection. On 13/12/2018: This issue was corrected from previous inspection. DEA of factory building was reaccepted by ACCORD on 28-Nov-2018. On 04-Jul-2019 : Corrected from previous inspection. The DEA was re-accepted from ACCORD on 28-Nov-2018. On 16-Feb-2020: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of Building-2 was previously accepted. On 02-Jan-2022: DEA of building-2 has been re-accepted from ACCORD on 28th November 2018. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. On 03-Apr-2023: This issue was corrected from previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. On 5-Jan-2025: Corrected previously. | Priority 1 (Immediate -Now) | Corrected
Initial Inspection |  | 2 | Columns appear to be stressed to a high level and require immediate review. | Loads to be maintained/reduced to 1.5kPa in area highlighted at all suspended levels | Corrected | Nov 30 2014 | On 28/06/2015: The factory maintaining initial report instruction except 1st floor area. Presently in 1st floor area have 63.00psf loading. On 18/08/2015: The factory maintain initial report instruction. On 25/07/2016: Found incorrect; no load plan found posted during inspection. Loading found satisfactory(<30 psf) according to initial report. On 26/02/2017: During inspection, Loading on the highlighted area of suspended slab was found within 1.5 Kpa. Safe load plan was found posted on each floor. On 30-May-2017: Loading was found as per safe load plan which was found posted at floors. On 03-12-2017: Found corrected in previous inspection. During inspection, loads were found within allowable load 1.5 Kpa. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. Floor load was found below 1.5 kPa. On 13/12/2018: This issue was corrected from previous inspection. During inspection, loading was found within posted safe load plan limit. ( 20 psf). On 04-Jul-2019 : Corrected from previous inspection. The retrofitting work was found on going. Safe load plan was found posted. Load was found below mentioned load limit (30 psf). On 16-Feb-2020: This issue was corrected from previous inspection. The DEA building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 13-Sep-2021: This issue was corrected in previous follow-up inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). On 5-Jan-2025: Corrected previously. (see CAP item-59). | Priority 1 (Immediate -Now) | Corrected
Initial Inspection |  | 3 | Columns appear to be stressed to a high level and require immediate review. | Verify insitu concrete strength either by 100mm diameter cores or existing cylinder strength data for cores from 4 columns . Verify grade of steel reinforcement used. | Corrected | Nov 30 2014 | On 28/06/2015: The factory already completed core cutting works. On 18/08/2015: The factory already completed core cutting works. On 25/07/2016: Core test has been done. This issue will be covered in DEA report & its verification. On 26/02/2017: Factory has taken cores from columns, beams & slabs to verify concrete strength as a part of DEA. During inspection, original core test report was available for slabs and beams but original core test report from column was not available. On 30-May-2017: Provided core test reports with DEA were available onsite. During inspection, extra cores at 3F columns & ground floor column were found but no test report was shown of these cores. Factory engineer is required to provide clarification for those extra cores. Also provided core cutting layout found mismatched with site condition. Need to update the core cutting layout before next follow up inspection. On 03-12-2017: Factory engineer taken 14 cores from column , beam and slab to determine the equivalent concrete strength which was observed during inspection. Some extra-core locations were also observed and factory told that some cores were damaged during extracting. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected form previous follow up inspection. Core was taken as a part of concrete strength evaluation and core test location was verified in previous inspection. The issue is corrected as per previous inspection. On 13/12/2018: This issue was corrected from previous inspection. During inspection, original core test report was found. On 04-Jul-2019 : Corrected from previous inspection. During inspection, core test reports were found. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: Core was taken as a part of concrete strength evaluation and core test location was verified in previous inspection. The issue is corrected as per previous inspection. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. Core was taken as a part of DEA. On 02-Jan-2022: Cores were taken as a part of DEA. Original reports were available onsite. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 1 (Immediate -Now) | Corrected
Initial Inspection |  | 4 | Columns appear to be stressed to a high level and require immediate review. | A Detail Engineering Assessment of Factory to be commenced, see attached Scope. | Corrected | Nov 30 2014 | On 28/06/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On verification period factory management didn’t shown any DEA copy because in factory level no DEA report copy. On 18/08/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: Factory completed DEA and submitted to ACCORD which was accepted on 26/01/2017. On 30-May-2017: A Detail Engineering Assessment was carried out by the factory which was accepted to ACCORD by where all structural element adequacies were covered. On 03-12-2017: Found corrected in previous inspection. A Detail Engineering Assessment(DEA) was carried out by the factory which was accepted from ACCORD. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. On 13/12/2018: This issue was corrected from previous inspection. DEA of factory building was reaccepted by ACCORD on 28-Nov-2018. On 04-Jul-2019 : Corrected from previous inspection. DEA of factory building was reaccepted by ACCORD on 28-Nov-2018. On 16-Feb-2020: This issue was corrected from previous inspection. DEA of building-2 was re-accepted by ACCORD on 28-Nov-2018. On 02-Feb-2021: This issue was corrected from previous inspection. DEA of building-2 was re-accepted by ACCORD on 28-Nov-2018. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. On 02-Jan-2022: DEA of building-2 was re-accepted from ACCORD on 28th November 2018. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. On 03-Apr-2023: This issue was corrected from previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. On 5-Jan-2025: Corrected previously. | Priority 1 (Immediate -Now) | Corrected
Initial Inspection |  | 5 | Columns appear to be stressed to a high level and require immediate review. | Detail Engineering Assessment to be completed. | Corrected | Nov 30 2014 | On 28/06/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On verification period factory management didn’t shown any DEA copy because in factory level no DEA report copy. On 18/08/2015: The factory already completed an DEA report and submitted to ACCORD and DEA is under review. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: Factory completed DEA and submitted to ACCORD which was accepted on 26/01/2017. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 30-May-2017: DEA has been accepted from ACCORD. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 03-12-2017: DEA was carried out by the factory which got acceptance from ACCORD with the recommendation of some retrofitting works. Factory was not meet the retrofitting time line given from Accord that was November 30, 2017. During inspection it was observed that, factory start their remediation work by dismantling the ground floor base for foundation retrofitting. This issue will be corrected after completion of retrofitting work. On 31/12/2017: DEA was carried out by the factory which got acceptance from ACCORD with the recommendation of some retrofitting works. Retrofitting work for building-2 was ongoing during inspection. On 16/07/2018: DEA documents of the factory were accepted by Accord on 26/01/2017. Factory has revised DEA report due to retrofit complication on existing condition and submitted to Accord on 28-Feb-2018. A review mail was sent from Accord on 12 March 2018 but till the date of inspection DEA was not submitted to Accord. Factory is required to submit DEA to Accord. On 13/12/2018: DEA of factory building was reaccepted by ACCORD on 28-Nov-2018. Factory is required to complete retrofitting works within 31st March 2019. During inspection, retrofitting work was found started. Factory is required to ensure construction safety measures & complete retrofitting works within given timeline. On 04-Jul-2019 : DEA of factory building was reaccepted by ACCORD on 28-Nov-2018. The retrofitting work was found on going. On 16-Feb-2020: DEA of building-2 was reaccepted by ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. Retrofitting completion certificate for building-2 was also found on site from consultant side. On 02-Feb-2021: This issue was corrected from previous inspection. DEA of building-2 was reaccepted by ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. On 02-Jan-2022: DEA was re-accepted from ACCORD on 28th November 2018. As per DEA, factory has completed all the required remediation. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. Retrofitting was completed. On 03-Apr-2023: This issue was corrected from previous inspection. DEA of Building-2 has been re-accepted from ACCORD on 28th November 2018. As per DEA recommendation remedial works were completed. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 6 | Columns appear to be stressed to a high level and require immediate review. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected | Nov 30 2014 | On 28/06/2015: Up to approve DEA report the factory should be maintain initial report instruction. On 18/08/2015: Up to approve DEA report the factory should be maintain initial report instruction. On 25/07/2016: Found incorrect; no load plan found posted during inspection. Loading found satisfactory(<30 psf) according to initial report. On 26/02/2017: Load Plan has been prepared as a part of DEA which was accepted by ACCORD on 26/01/2017. During inspection, Loading was found within limit as per safe load Plan. Safe load plan was found posted on each floor. Factory shall manage final load plan after completion of retrofitting. Retrofitting work has not been started yet. On 30-May-2017: DEA has been accepted from ACCORD. During inspection, floor loading was found as per safe load plan. On 30-May-2017: A Detail Engineering Assessment was carried out by the factory which was accepted to ACCORD by where all structural element adequacies were covered. On 03-12-2017: Allowable safe load plan was prepared by the factory which was accepted from ACCORD. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. On 31/12/2017: Load plan has been produced and accepted along with DEA. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. On 16/07/2018: A set of load plan has been prepared along with DEA. DEA was accepted by Accord on 26/01/2017 . Factory was submitted revised DEA on 28 Feb 2018 and a review mail was sent from Accord on 12th Mar 2018, but till the date of inspection DEA was not submitted to Accord. During inspection, load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the DEA re-acceptance. On 13/12/2018: Load plan was produced as part of DEA. Factory posted safe load plan. Loading was found within allowable limit of posted load plan (20 psf). Factory is required to post final load plan after completion of retrofitting works. On 04-Jul-2019 : Load plan has been produced as part of the DEA. The retrofitting work was found on going. Safe load plan was found posted. Load was found below mentioned load limit (30 psf). Final load plan is required to be posted after completing the remedial works. On 16-Feb-2020: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. After retrofitting load plan was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. On 5-Jan-2025: Corrected previously. (see CAP item-59). | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 7 | Columns appear to be stressed to a high level and require immediate review. | Continue to implement load plan. | Corrected | Dec 30 2014 | On 28/06/2015: Up to approve DEA report the factory should be maintain initial report instruction. On 18/08/2015: Up to approve DEA report the factory should be maintain initial report instruction. On 25/07/2016: Found incorrect; no load plan found posted during inspection. Loading found satisfactory(<30 psf) according to initial report. On 26/02/2017: Load Plan has been prepared as a part of DEA which was accepted by ACCORD on 26/01/2017. During inspection, Loading was found within limit as per safe load Plan. Safe load plan was found posted on each floor. Factory shall manage final load plan after completion of retrofitting. Retrofitting work has not started yet. On 30-May-2017: DEA has been accepted from ACCORD. During inspection, floor loading was found as per safe load plan. On 03-12-2017: Allowable safe load plan was prepared by the factory which was accepted from ACCORD. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. On 31/12/2017: Load plan has been produced and accepted along with DEA. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. Factory shall follow the final load plan after completion of retrofitting work. On 16/07/2018: A set of load plan has been prepared along with DEA. DEA was accepted by Accord on 26/01/2017 . Factory was submitted revised DEA on 28 Feb 2018 and a review mail was sent from Accord on 12th Mar 2018, but till the date of inspection DEA was not submitted to Accord. During inspection, load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the DEA re-acceptance. On 13/12/2018: Load plan was produced as part of DEA. Factory posted safe load plan. Loading was found within allowable limit of posted load plan (20 psf). Factory is required to post final load plan after completion of retrofitting works. On 04-Jul-2019 : Load plan has been produced as part of the DEA. Safe load plan was found posted. Load was found below mentioned load limit (30 psf). Final load plan is required to be posted after completing the remedial works. On 16-Feb-2020: The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. After retrofitting load plan was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. On 5-Jan-2025: Corrected previously. (see CAP item-59). | Priority 3 (within 6-months) | Corrected
Initial Inspection |  | 8 | Management of floor storage loads and structural adequacy of slab to support floor build-up loads in toilet areas. | Extent of build-up loading within toilet areas to be surveyed and capacity of floor slab to be assessed to confirm that the floor slab is designed to carry these loads. | Corrected | Nov 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 26/01/2017. As per DEA, slab was found adequate to carry loads. On 30-May-2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 26/01/2017. As per DEA, slab was found adequate to carry loads. On 03-12-2017: Found corrected in previous inspection. A detailed engineering assessment was carried out addressing mentioned issues. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. On 13/12/2018:This issue was corrected from previous inspection. As per accepted DEA, slab is adequate. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. After retrofitting load plan was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA of factory Building-2 was reaccepted by ACCORD on 28-Nov-2018. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 9 | Management of floor storage loads and structural adequacy of slab to support floor build-up loads in toilet areas. | Produce and actively manage a loading plan for all floor plates within the factory giving consideration to floor capacity and column capacity. | Corrected | Nov 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: Load Plan has been prepared as a part of DEA which was accepted by ACCORD on 26/01/2017. During inspection, Loading was found within limit as per safe load Plan. Safe load was found posted on each floor. Factory shall manage final load plan after completion of retrofitting. Retrofitting work has not been started yet. On 30-May-2017: DEA has been accepted from ACCORD. During inspection, floor loading was found as per safe load plan. On 03-12-2017: Allowable safe load plan was prepared by the factory which was accepted from ACCORD. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. On 31/12/2017: Load plan has been produced and accepted along with DEA. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. On 16/07/2018: A set of load plan has been prepared along with DEA. DEA was accepted by Accord on 26/01/2017 . Factory was submitted revised DEA on 28 Feb 2018 and a review mail was sent from Accord on 12th Mar 2018, but till the date of inspection DEA was not submitted to Accord. During inspection, load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the DEA re-acceptance. On 13/12/2018: Load plan was produced as part of DEA. Factory posted safe load plan. Loading was found within allowable limit of posted load plan (20 psf). Factory is required to post final load plan after completion of retrofitting works. On 04-Jul-2019 : Load plan has been produced as part of the DEA. Safe load plan was found posted. Load was found below mentioned load limit (30 psf). Final load plan is required to be posted after completing the remedial works. On 16-Feb-2020: The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. After retrofitting load plan was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. On 5-Jan-2025: Corrected previously. (see CAP item-59). | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 10 | Management of floor storage loads and structural adequacy of slab to support floor build-up loads in toilet areas. | Continue to implement load plan. | Corrected | Dec 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: Load Plan has been prepared as a part of DEA which was accepted by ACCORD on 26/01/2017. During inspection, Loading was found within limit as per safe load Plan. Safe load was found posted on each floor. Factory shall manage final load plan after completion of retrofitting. Retrofitting work has not been started yet. On 30-May-2017: DEA has been accepted from ACCORD. During inspection, floor loading was found as per safe load plan. On 03-12-2017: Allowable safe load plan was prepared by the factory which was accepted from ACCORD. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable limit 42 psf. On 31/12/2017: Load plan has been produced and accepted along with DEA. Factory is required to follow safe load plan until the completion of retrofitting work. During inspection, loads were found within allowable safe load limit 42 psf. Factory shall follow the final load plan after completion of retrofitting work. On 16/07/2018: A set of load plan has been prepared along with DEA. DEA was accepted by Accord on 26/01/2017 . Factory was submitted revised DEA on 28 Feb 2018 and a review mail was sent from Accord on 12th Mar 2018, but till the date of inspection DEA was not submitted to Accord. During inspection, load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the DEA re-acceptance. On 13/12/2018: Load plan was produced as part of DEA. Factory posted safe load plan. Loading was found within allowable limit of posted load plan (20 psf). Factory is required to post final load plan after completion of retrofitting works. On 04-Jul-2019 : Load plan has been produced as part of the DEA. Safe load plan was found posted. Load was found below mentioned load limit (30 psf). Final load plan is required to be posted after completing the remedial works. On 16-Feb-2020: The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 02-Feb-2021: This issue was corrected from previous inspection. The DEA of building-2 was re-accepted from ACCORD on 28-Nov-2018. The retrofitting work of building-2 was found completed. After retrofitting load plan was found posted. Load was found below mentioned load limit (63 psf). On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA of factory building-2 was reaccepted by ACCORD on 28-Nov-2018. Retrofitting was completed. After retrofitting load plan was posted. Loading was found within 63 psf. On 02-Jan-2022: Factory has completed the remediation. However, floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. After retrofitting load plan(63 psf) was posted. Loading was found within 63 psf. On 03-Apr-2023: This issue was corrected from previous inspection. Floor loading was found below the allowable limit of final load plan (63psf). Load plans were found posted in each floor. On 5-Jan-2025: Corrected previously. (see CAP item-59). | Priority 3 (within 6-months) | Corrected
Initial Inspection |  | 11 | Mezzanine slab and support columns. | Remove storage loads from mezzanine. | Corrected | Aug 7 2014 | On 28/06/2015: The factory already removed mezzanine floor structure. Finally its cover in DEA report. On 18/08/2015: The factory already removed mezzanine floor structure. Finally its cover in DEA report. On 25/07/2016: Corrected; Mezzanine floor found removed. On 26/02/2017:Factory has demolished the mezzanine floors and maintaining safe load plan On 30-May-2017: Mezzanine floor found demolished and storage was removed. On 03-12-2017: Found corrected in previous inspection. During inspection, mezzanine slabs were found demolished. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. Factory had demolished the mezzanine floors On 13/12/2018: This issue was corrected from previous inspection. Mezzanine floor has been demolished. On 04-Jul-2019 : Corrected from previous inspection. Mezzanine floor found demolished. On 16-Feb-2020: This issue was corrected from previous inspection. The factory already removed mezzanine floor structure. On 02-Feb-2021: This issue was corrected from previous inspection. The factory already removed mezzanine floor structure. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. The mezzanine floor was removed. On 02-Jan-2022: Mezzanine floor has been removed. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. The mezzanine floor was removed. On 03-Apr-2023: This issue was corrected from previous inspection. Mezzanine floor was demolished previously. On 5-Jan-2025: Corrected previously. Mezzanine floor was demolished previously. | Priority 1 (Immediate -Now) | Corrected
Initial Inspection |  | 12 | Mezzanine slab and support columns. | Building Engineer to verify structural adequacy of this arrangement –slab, column and transfer beam arrangement. Note that in a number of instances mezzanine columns appear to be supported directly from the floor slabwithout transfer beams. | Corrected | Dec 30 2014 | On 28/06/2015: The factory already removed mezzanine floor structure. Finally its cover in DEA report. On 18/08/2015: The factory already removed mezzanine floor structure. Finally its cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017:This issue was covered in DEA. Factory has done DEA which was accepted by ACCORD on 26/01/2017. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 30-May-2017: DEA has been accepted from ACCORD. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 03-12-2017: A detail engineering assessment was carried out addressing mentioned issues which got acceptance from accord with some recommendations. Factory engineer taken 14 cores from column , beam and slab to determine the equivalent concrete strength which was observed during inspection. Some extra-core locations were also observed and factory told that some cores were damaged during extracting. On 31/12/2017: During inspection, mezzanine slabs were found demolished. On 16/07/2018: Found corrected from previous follow up inspection. Factory had demolished the mezzanine floors On 13/12/2018: This issue was corrected from previous inspection. Mezzanine floor has been demolished. On 04-Jul-2019 : Corrected from previous inspection. Mezzanine floor found demolished. On 16-Feb-2020: This issue was corrected from previous inspection. The factory already removed mezzanine floor structure. On 02-Feb-2021: This issue was corrected from previous inspection. The factory already removed mezzanine floor structure. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. The mezzanine floor was removed. On 02-Jan-2022: Mezzanine floor has been removed. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. The mezzanine floor was removed. On 03-Apr-2023: This issue was corrected from previous inspection. Mezzanine floor was demolished previously. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 13 | Check beam design for suspended rack/trolley system. | Building Engineer to verify structural adequacy of the floor beams to support floor loads and additional loads due to suspended rack/trolley system. | Corrected | Nov 30 2014 | On 28/06/2015: The factory engineer & consultant engineer check all crack and finally its cover in DEA report. On 18/08/2015: The factory engineer & consultant engineer check all crack and finally its cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: This issue was covered in DEA. Factory has done DEA which was accepted by ACCORD on 26/01/2017. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date On 30-May-2017: DEA has been accepted from ACCORD. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 03-12-2017:A Detail Engineering Assessment(DEA) was carried out by the factory which was accepted from ACCORD where all the beams are found adequate considering suspended racks/trolley system. On 31/12/2017: As per accepted DEA all the beams are found adequate considering suspended racks/trolley system. On 16/07/2018: Found corrected from previous follow up inspection. On 13/12/2018:This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: All beams were found adequate considering suspended rack system. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. As per accepted DEA all the beams are found adequate considering suspended racks/trolley system. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 14 | Lateral stability of steel frame to roof Dining Area. | Building Engineer to verify structural adequacy of this arrangement and design bracing system to be installed if required. | Corrected | Nov 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: This issue was covered in DEA. Factory completed DEA and submitted to ACCORD which was accepted on 26/02/2017. As per accepted DEA, column and sub beam were found overstressed. The vertical extension the shed will be demolished otherwise roof top area have to be retrofitted. On 30-May-2017: DEA has been accepted from ACCORD. As per accepted DEA, retrofitting is required to the factory building. Retrofitting has not been started till inspection date. On 03-12-2017: Lateral stability of the roof top dining area has been checked under DEA which got accepted from Accord. As per the recommendation from DEA, the structure will be vertically extended, that's why dining area will be demolished in future. On 31/12/2017: As per the recommendation from DEA, the structure will be vertically extended, that's why dining area will be demolished in future. During inspection, no extension or demolition work was seen on roof. On 16/07/2018: DEA documents of the factory were accepted by Accord on 26/01/2017. Factory has revised DEA report due to retrofit complication on existing condition and submitted to Accord on 28-Feb-2018. A review mail was sent from Accord on 12 March 2018 but till the date of inspection DEA was not submitted to Accord. Factory is required to submit DEA to Accord.. On 13/12/2018: This issue has been cover in DEA. DEA of factory building was reaccepted by ACCORD on 28th November 2018. As per accepted DEA, factory is required to demolished steel frame to roof dinning area. Factory is required to complete remedial works within 31st March 2019. On 04-Jul-2019 : According to reaccepted DEA, the roof shed is required to be removed, which has not been done yet. On 16-Feb-2020: During inspection, roof dinning shed of building-2 was found demolished. On 02-Feb-2021: This issue was corrected from previous inspection. During inspection, roof dinning shed of building-2 was found demolished. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. Roof dinning shed on Building-2 was demolished. On 02-Jan-2022: Roof dining shed has been demolished. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Roof dining shed has been demolished. On 03-Apr-2023: This issue was corrected from previous inspection. Roof dinning shed was demolished previously. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 15 | Check on column crack/damage in one location –see photos. | Building Engineer to investigate if cracking is superficial only and carry out repairs or strengthening as required. | Corrected | Nov 30 2014 | On 28/06/2015: The factory engineer & consultant engineer check all crack and finally its cover in DEA report. On 18/08/2015: The factory engineer & consultant engineer check all crack and finally its cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: During inspection, the crack column was found plastered. However, As per DEA recommendation, Factory required to install props up to 2nd floor slab until taking in hand of retrofitting of column. Factory is required to install props as per engineer's advice. On 30-May-2017: During inspection, no crack was visible at column. Also props have been found installed at individual locations.. On 03-12-2017:Found corrected in previous inspection. During inspection, No cracks were observed. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. During inspection, No visible cracks were observed. On 13/12/2018:This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. During inspection, No visible cracks were found. On 02-Feb-2021: This issue was corrected from previous inspection. During inspection, No visible cracks were found. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. No crack was found during inspection. On 02-Jan-2022: No cracks were found during inspection. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. No crack was found during inspection. On 03-Apr-2023: This issue was corrected from previous inspection. During inspection, No visible cracks were found. On 5-Jan-2025: Corrected previously. No crack was found on column. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 16 | Anchorage of communication masts on Building 2 roof. | Building Engineer to check and verify anchorage of communication masts on Building 2 roof. | Corrected | Nov 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: This issue was covered in DEA. Factory completed DEA which was accepted by ACCORD on 26/01/2017. Anchorage of the communication mast was checked and found ok. On 30-May-2017: This issue was covered in DEA. Factory completed DEA which was accepted by ACCORD on 26/01/2017. Anchorage of the communication mast was checked and found ok. On 03-12-2017:Found corrected in previous inspection. Mentioned issue was covered in DEA. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. Anchorage of the communication mast was checked and found satisfactory. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 17 | Water causing damage and corrosion. | Engineer to inspect water damaged structure including the exterior and propose a suitable repair. Roof drainage system to be upgraded as necessary and new downpipes installed where required. | Corrected | Aug 7 2014 | On 25/07/2016: Corrected in 1st follow up; found same in current. On 26/02/2017: Corrected in previous follow up inspection report On 30-May-2017: Corrected in the previous follow up inspection. No water causing damaged found during inspection. On 03-12-2017:Found corrected in previous inspection. During inspection, no dampness were observed. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Corrected from previous inspection. no dampness were observed. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. No water causing damaged found during inspection. No water ponding was found at roof floor. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. No water ponding was found during inspection. On 02-Jan-2022: No water ponding was found at roof. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. No water ponding was found during inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. Factory had provided rust-proof paint on exposed rebar. For dampness see CAP item-51. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 18 | Remove steel stored on roof of Building 1/Building 2 link. | Stored structural steel beams to be removed from roof level and stored at ground level. | Corrected | Aug 7 2014 | On 28/06/2015: Presently have some steel materials storage in roof top. On 18/08/2015: Presently have some steel materials storage in roof top. On 25/07/2016: Corrected; Structural steel beams were removed from building 1 & 2 link. On 26/02/2017: Structural steel beams were removed from building 1 & 2 link. On 30-May-2017: Structural steel beams were removed from building 1 & 2 link. On 03-12-2017:Found corrected in previous inspection. Mentioned issue was covered in DEA. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Structural steel beams were removed from building 1 & 2 link. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. No storage was found at roof of building1/Building2. On 5-Jan-2025: Corrected previously. No store was found on roof of Building-2. | Priority 2 (within 6-weeks) | Corrected
Initial Inspection |  | 19 | Discrepancies between structural details provided and the as-constructed building. | Building Engineer to survey as-built structure and prepare accurate as-built survey information, including all columns, beams and slabsas part of DEA. | Corrected | Nov 30 2014 | On 28/06/2015: Cover in DEA report. On 18/08/2015: Cover in DEA report. On 25/07/2016: This issue is required to be covered in DEA report. Factory management submitted their DEA report to ACCORD which is under review. On 26/02/2017: Factory prepared As- Built drawing of the factory building which was accepted by ACCORD on 26/01/2017. During inspection, Some discrepancy was found in As- Built drawings. Factory is required to revised the drawings. On 30-May-2017:During inspection, both as built architectural & structural drawing for 5F was found produced and submitted to ACCORD. On 03-12-2017:Found corrected in previous inspection. Factory prepared As- Built drawing of the factory building as part of DEA which got accepted by ACCORD. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Corrected from previous inspection. On 16/07/2018: Corrected from previous inspection. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019 : Corrected from previous inspection. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Factory prepared As- Built drawing of the factory building as part of DEA which got accepted by ACCORD. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: A set of as-built drawing has been prepared as a part of DEA which has been re-accepted from ACCORD on 28th November 2018. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. A set of as-built drawing has been prepared as a part of DEA which has been re-accepted from ACCORD on 28th November 2018. On 03-Apr-2023: This issue was corrected from previous inspection. A set of as-built drawing has been prepared as a part of DEA which has been re-accepted from ACCORD on 28th November 2018. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 20 | New Findings-1: Uncontrolled heavy storage loading in Building 1. | Reduce stacking height to ensure total load does not exceed 2.0 kPa | Corrected | Dec 31 2017 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, no marking was observed for stacking height for controlling live load. However, loads were measured and found above 2.Kpa. Factory is required to keep load below 2.0 KPa. On 31/12/2017: During inspection, loads found above 2.Kpa at fabric store. Later factory reduce load from store and provide picture by mail. Factory is required to keep load below 2.0 KPa. On 16/07/2018: Found corrected from previous follow up inspection. Floor load was found below 42 psf. On 13/12/2018: This issue was corrected from previous inspection. During inspection, loading was found within 2 Kpa. On 04-Jul-2019: Corrected previously. Loading was found within 2kPa. On 16-Feb-2020: This issue was corrected from previous inspection. During inspection, building was found fully evacuated. On 02-Feb-2021: This issue was corrected from previous inspection. Load plan of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. Loading was found within 3 kpa. On 02-Jan-2022: Floor loading was found below 3 kPa. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Loading was found within 3 kPa as per accepted load plan. | Priority 1-( Immediate – Now) | Corrected
Follow Up Inspection |  | 21 | New Findings-2: Uncontrolled heavy storage loading in Building 1. | An Engineering Assessment id required to review the design and loads. | Corrected | Dec 31 2017 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory reviewed the design and loads as a part of DEA. On 31/12/2017: Corrected in previous inspection. Factory has prepared EA for Building-1 and submitted to Accord. On 16/07/2018: This issue was corrected from previous inspection. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019: Corrected previously. On 16-Feb-2020: This issue was corrected from previous inspection. DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. On 02-Feb-2021: This issue was corrected from previous inspection. DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: DEA of building-1 has been accepted with proposed vertical extension of six storied from ACCORD on 15th September 2019. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. On 03-Apr-2023: This issue was corrected from previous inspection. DEA of Building-1 (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. During inspection, Building-1 was found 5 storied. On 5-Jan-2025: Corrected previously. | Priority 1-( Immediate – Now) | Corrected
Follow Up Inspection |  | 22 | New Findings-3: Uncontrolled heavy storage loading in Building 1. | Factory Engineer to state the maximum weight that is allowed per square meter. Suggest that state the value on notice boards in these areas. (LoadingPlans). | Corrected | Dec 31 2017 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, loads were found above 2 KPa. Factory is required to set a load programmed so that maximum load does not exceed 2 KPa. On 31/12/2017: During inspection, loads found above 2.Kpa at fabric store. Later factory reduce load from store and provide picture by mail. Factory is required to keep load below 2.0 KPa. On 16/07/2018: Found corrected from previous follow inspection. Floor load was found below 42 psf. On 16/07/2018: This issue was corrected from previous inspection. On 13/12/2018: This issue was corrected from previous inspection. During inspection, loading was found within 2Kpa. On 04-Jul-2019: Corrected previously. On 16-Feb-2020: This issue was corrected from previous inspection. DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. On 02-Feb-2021: This issue was corrected from previous inspection. Load plan of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. Heavy storage loading was not observed. See item number- 38. On 02-Jan-2022: Issue was found corrected from previous follow up inspection. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Load plan was found posted on floors. Loading was found within 3 kPa. | Priority 1-( Immediate – Now) | Corrected
Follow Up Inspection |  | 23 | New Findings-4: Uncontrolled heavy storage loading in Building 1. | Reduce stacking height to ensure total load does not exceed 2.0 kPa | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, no marking or sign was observed to follow load at stacking. However, loads were observed above 2 KPa. Factory is required to mark the stacking height so that live load does not exceed 2 KPa. On 31/12/2017: During inspection, loads found above 2.Kpa at fabric store. Later factory reduce load from store and provide picture by mail. Factory is required to keep load below 2.0 KPa until DEA acceptance. On 16/07/2018: During inspection, floor load was found below 42 psf. Factory is required to maintain before retrofit load plan (42 psf) until EA acceptance. On 16/07/2018: Load plan has been produced as part of DEA. Revised DEA has been submitted to ACCORD on 11th December 2018 which is under review. During inspection, loading was found within 2 Kpa. Factory will post final load plan as per accepted DEA documents. On 13/12/2018: Load plan has been produced as part of DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. During inspection, loading was found within 2 Kpa. Factory is required to post final load plan after acceptance of DEA as per accepted documents. On 04-Jul-2019: Overall loading in building-1 was found within 2kPa. On 16-Feb-2020: On 16-Feb-2020: This issue was corrected from previous inspection. DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. On 02-Feb-2021: This issue was corrected from previous inspection. Load plan of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. DEA was accepted along with load plan. Stack height was reduced. See item number- 38. On 02-Jan-2022: Load plans were prepared along with DEA. Floor loading was found below the allowable load limit (3kPa). Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Loading was found within 3 kpa. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 24 | New Findings-5: Uncontrolled heavy storage loading in Building 1. | Maintain standards of quality control to ensure that storage procedures are correctly followed so that overloading problems do not arise in the future. | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, loads were observed above 2 KPa. Factory is required to follow allowable safe load plan so that overloading problems do not arise in the future. On 31/12/2017: During inspection, loads found above 2.Kpa at fabric store. Later factory reduce load from store and provide picture by mail. Factory is required to follow allowable safe load plan so that overloading problems do not arise in the future. On 16/07/2018: A set of load plan has been prepared along with EA which is not accepted yet. Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. During inspection, safe load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the EA acceptance. On 16/07/2018: Load plan has been produced as part of DEA. Revised DEA has been submitted to ACCORD on 11th December 2018 which is under review. During inspection, loading was found within 2 Kpa. Factory will post final load plan as per accepted DEA documents. On 13/12/2018: Load plan has been produced as part of DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. During inspection, loading was found within 2 Kpa. Factory is required to post final load plan after acceptance of DEA as per accepted documents. On 04-Jul-2019: Load plans have been produced as part of DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. During inspection, loading was found within 2kPa. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. After completion of retrofitting factory is required to follow the accepted final load plan. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated and retrofitting and demolition work was ongoing. After completion of retrofitting factory is required to follow the accepted final load plan On 13-Sep-2021: Currently the building is 4 storied(3rd and 4th floor partition walls were not constructed till inspection date). The building is approved for six story. Loading was found within 3 kPa. Retrofitting was completed considering 6 story. Factory is required to post and maintain accepted load plan. On 02-Jan-2022: Loading was found within 3 kPa. Vertical extension works were found ongoing. DEA of proposed 6-storied has been accepted from ACCORD on 15th September 2019. Now, the factory is required to follow the accepted drawing in extension works. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Loading was found within 3 kpa. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 25 | New Findings-6: Uncontrolled heavy storage loading in Building 1. | Maintain and implement Loading Plans. | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied building-1 which is not covered in ARUP inspected initial report . But another initial report was found for the mentioned building which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, no marking or sign was observed to follow live load. Factory is required to follow allowable safe load plan so that overloading problems do not arise in the future. On 31/12/2017: Factory has prepared a load plan along with EA for building-1 and submitted to Accord which is not accepted yet. Factory shall post the accepted load plan and maintain accordingly. On 16/07/2018: A set of load plan has been prepared along with EA which is not accepted yet. Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. During inspection, safe load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the EA acceptance. On 16/07/2018: Load plan has been produced as part of DEA. Revised DEA has been submitted to ACCORD on 11th December 2018 which is under review. During inspection, loading was found within 2 Kpa. Factory will post final load plan as per accepted DEA documents. On 13/12/2018: Load plan has been produced as part of DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. During inspection, loading was found within 2 Kpa. Factory is required to post final load plan after acceptance of DEA as per accepted documents. On 04-Jul-2019: Load plans have been produced as part of DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. During inspection, loading was found within 2kPa. Factory is required to maintain accepted load plan limit after acceptance. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. The factory had commenced retrofitting work but could not continue. During inspection no retrofitting was found on going. After completion of retrofitting factory is required to follow the accepted final load plan. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going. After completion of retrofitting factory is required to follow the accepted final load plan. On 13-Sep-2021: Currently the building is 4 storied(3rd and 4th floor partition walls were not constructed till inspection date). The building is approved for six story. Loading was found within 3 kPa. Retrofitting was completed considering 6 story. Factory is required to post and maintain accepted load plan. On 02-Jan-2022: Loading was found within 3 kPa. Vertical extension works were found ongoing. DEA of proposed 6-storied has been accepted from ACCORD on 15th September 2019. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Loading was found within 3 kpa. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 26 | New Findings-7: Construction materials on the top of the connection link | Remove construction materials in the area identified above | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Construction materials were found removed from the connection link. On 31/12/2017: Corrected from previous inspection. Comments are same as previous. On 16/07/2018: Found corrected from previous follow up inspection. On 16/07/2018: This issue was corrected from previous inspection. On 13/12/2018:This issue was corrected from previous inspection. On 04-Jul-2019: Corrected previously. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Link connection portion was found demolished. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. On 02-Jan-2022: Link connection was found demolished. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Link connection portion was found demolished. On 03-Apr-2023: This issue was corrected in previous follow-up inspection. Link connection portion was found demolished. A new lift core was found under constructed in place of connection link. On 5-Jan-2025: Corrected previously. A new lift core was found in place of connection link. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 27 | New Findings-8: Capacity check of cantilevered slab supporting steel column in Dyeing Shed. | Factory Engineer to review design, loads and related elements in area identified above to confirm capacity for these items | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this dyeing shed which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. The revised DEA of the building has not submitted yet to ACCORD. Factory is required to submit the document as soon as possible. On 31/12/2017: Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised DEA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to implement remedial works after DEA acceptance if required. On 16-Feb-2020: Factory had produced EA report for the dyeing shed, which was accepted from ACCORD on 12th February 2020, During inspection, some mismatch was found in column size, Factory is required to revised the documents and submit to ACCORD within given timeline. As per EA recommendation retrofitting work has not started yet, where remediation timeline is 15th April 2020. On 02-Feb-2021: Factory had revised the EA report for the dyeing shed, which was re-accepted from ACCORD on 22th May 2020. As per EA recommendation some retrofitting is required for Dyeing shed. During inspection, it was found that retrofitting work has not started yet, where remediation time line was 15th July 2020. On 13-Sep-2021: As per accepted EA, retrofitting works were completed for Dyeing shed. During inspection, some mismatches were found in retrofitting drawings. After inspection factory submitted revised drawings which was found satisfactory. On 02-Jan-2022: A set of as-built drawing has been prepared along with DEA. DEA was accepted on 12th February 2020. Factory has completed all the required remediation. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA was accepted on 12th February 2020. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 28 | New Findings-9: Incomplete structural drawings | Factory Engineer to survey the actual conditions and revise the drawings. | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, No Prepared drawing hard copies were observed onsite. This issue will be cover in DEA. On 31/12/2017: Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: A set of as-built drawing has been prepared along with EA which is not accepted yet. Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: As built drawing has been produced as part of DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Till the date of inspection, factory hadn't submitted any documents to Accord. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: A set of as built drawing was produced as part of DEA of Building-1 Four-Storied Building (Proposed Six-Storied) and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: A set of as built drawing was produced as part of DEA of Building-1 Four-Storied Building (Proposed Six-Storied) and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: For Building-1, some beams(FB-2 stair beam) were not retrofitted. Additional toilet part was constructed in 2nd floor. After inspection, factory sent FEM and drawings claiming those beams did not require retrofitting. The documents were checked and found no additional retrofitting was required. On 02-Jan-2022: Issue was found corrected from previous follow up inspection. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 29 | New Findings -10: Incomplete structural drawings | Any recommendations of the Engineering Assessment which affect the structure should be taken on board | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, No Prepared drawing hard copies were observed onsite. This issue will be cover in DEA. On 31/12/2017: Factory has submitted the revised DEA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. Factory shall implement the remedial works if required in accepted EA. On 16/07/2018: Strengthening works need to be carried out ( if required) after the EA acceptance from ACCORD On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to implement remedial works after DEA acceptance if required. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. The factory had commenced retrofitting work but could not continue. During inspection no retrofitting was found on going. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. Some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: For Building-1, some beams(FB-2 stair beam) were not retrofitted. Additional toilet part was constructed in 2nd floor. After inspection, factory sent FEM and drawings claiming those beams did not require retrofitting. The documents were checked and found satisfactory. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 30 | New Findings-11: Incomplete structural drawings | Continue to implement load plan | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, loads were measured above 2 KPa. Factory is required to follow allowable load plan so that overloading problem does not arise in future. On 31/12/2017: Factory has prepared a load plan along with EA and submitted to Accord which is not accepted yet. Factory shall post the accepted load plan and maintain accordingly. On 16/07/2018: A set of load plan has been prepared along with EA which is not accepted yet. Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. During inspection, safe load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the EA acceptance. On 13/12/2018: Load plan has been produced as part of DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. During inspection, loading was found within 2 Kpa. Factory is required to post final load plan after acceptance of DEA as per accepted documents. On 04-Jul-2019: Load plans have been produced as part of DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. During inspection, loading was found within 2kPa. Factory is required to maintain accepted load plan limit after acceptance. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. The factory had commenced retrofitting work but could not continue. During inspection no retrofitting was found on going. After completion of retrofitting factory is required to follow the accepted final load plan. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. After completion of retrofitting factory is required to follow the accepted final load plan. On 13-Sep-2021: For Building-1, some beams(FB-2 stair beam) were not retrofitted. Additional toilet part was constructed in 2nd floor. After inspection, factory sent FEM and drawings claiming those beams did not require retrofitting. The documents were checked and found satisfactory. Loading was found within 3kPa. On 02-Jan-2022: Loading was found within 3 kPa. Vertical extension works were found ongoing. DEA of proposed 6-storied has been accepted from ACCORD on 15th September 2019. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Loading was found within 3 kpa (As per accepted DEA-considering extension). On 03-Apr-2023: This issue was corrected from previous inspection. Load plan of Proposed 6 storied Building 1 ( current building is 5 storied) has been produced as part of DEA and accepted from ACCORD on 15th September 2019. Loading was found within 3 kpa. On 5-Jan-2025: Corrected previously. Loading was found within 3 kpa. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 31 | New Findings-12: Movement joint to be properly established at connection link | The Factory Engineer should investigate to prove the capacity of the building in its existing state, a further building approval should be gained for the building as it exists, as altered since the original approval. Alternatively, the extension building should be separated by a non-structural joint and allowed to act as a fully structurally independent structure | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: Connection link has not been considered in EA. Factory will demolish the connection link. During inspection, demolition work was on going. On 16/07/2018: Factory has demolished connection link. On 13/12/2018:This issue was corrected from previous inspection. Connection links has been demolished. On 04-Jul-2019: Corrected previously. Connection link was found demolished. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Connection link was found demolished. On 13-Sep-2021: This issue was corrected from previous inspection. Connection link was found demolished. On 02-Jan-2022: Connection link was found demolished. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Connection links has been demolished. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. A new lift core was found in place of the connection link. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 32 | New Findings-13: Movement joint to be properly established at connection link | Do not construct any further buildings connected to the existing building without thorough structural design and full building approval | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: Connection link has not been considered in EA. Factory will demolish the connection link. During inspection, demolition work was on going. On 16/07/2018: Factory has demolished connection link. On 13/12/2018:This issue was corrected from previous inspection. Connection links has been demolished. On 04-Jul-2019: Corrected previously. Connection link was found demolished. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Connection link was found demolished. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Connection links has been demolished. On 03-Apr-2023: This issue was corrected from previous inspection. Connection links has been demolished. On 5-Jan-2025: Corrected previously. A new lift core was found in place of the connection link. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 33 | New Findings-14: Capacity check of cantilevered slab supporting the water tanks in Building 1 and Building 3 | Factory Engineer to review design, loads and related elements in area identified above to confirm capacity for these items | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ARUP provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issues will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: The factory has prepared EA to review the capacity check of cantilevered slab supporting the water tanks which is not accepted yet. Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. During inspection, safe load plan was found posted in every floor and floor load was observed below allowable limit of floor load plan . Factory is required to maintain before retrofitting load plan until the EA acceptance. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement necessary remedial works if required. On 16-Feb-2020: DEA of Building-1 & 3 has produced and accepted from ACCORD. During inspection, building was found fully evacuated. Though the entry of building 1 was restricted, from the out side of the building-1 it was found that the extended cantilever slab and water tank was demolished. Also As per EA recommendation of building-3 cantilevered slab and water tanks was found demolished. On 02-Feb-2021: This issue was corrected from previous inspection. DEA of Building-1 & 3 has produced and accepted from ACCORD. During inspection, building-1 was found fully evacuated. The extended cantilever slab of building-1 and water tank was demolished. Also, as per DEA recommendation of building-3 cantilevered slab and water tanks was found demolished. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Cantilever slab has been demolished. No water tank was found. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Cantilever slab has been demolished. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 34 | New Findings-15: Capacity check of cantilevered slab supporting the water tanks in Building 1 and Building 3 | Remove water tanks in the area identified above | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. During inspection, water tank was found empty. Factory is required to take action removing water tanks. On 31/12/2017: Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement necessary remedial works if required. Water tanks were still in place. On 16-Feb-2020: DEA of Building-1 & 3 has produced and accepted from ACCORD. During inspection, building was found fully evacuated. Though the entry of building 1 was restricted, from the out side of the building-1 it was found that the extended cantilever slab and water tank was demolished. Also As per EA recommendation of building-3 cantilevered slab and water tanks was found demolished. On 02-Feb-2021: This issue was corrected from previous inspection. DEA of Building-1 & 3 has produced and accepted from ACCORD. During inspection, building-1 was found fully evacuated. The extended cantilever slab of building-1 and water tank was demolished. Also, as per DEA recommendation of building-3 cantilevered slab and water tanks was found demolished. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Cantilever slab has been demolished. No water tank was found. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Cantilever slab has been demolished. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 35 | New Findings-16: Capacity check of slab supporting chemical tanks in the Dyeing Shed | Factory Engineer to review design, loads and related elements in area identified above to confirm capacity for these items | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement necessary remedial works if required. Water tanks were still in place. On 16-Feb-2020: Factory had produced DEA report for the dyeing shed, which was accepted from ACCORD on 12th February 2020, As per DEA recommendation retrofitting work of Auto Dispense was found completed. On 02-Feb-2021: This issue was corrected from previous inspection. Factory had produced Capacity check of slab supporting chemical tanks for the Auto Dispensein the dyeing shed, which was accepted from ACCORD on 12th February 2020, As per DEA recommendation retrofitting work of Auto Dispense was found completed. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: DEA was accepted from ACCORD on 12th February 2020. Factory has completed all the required remediation. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA was accepted from ACCORD on 12th February 2020. Factory has completed all the required remediation. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 36 | New Findings-17: Capacity check of slab supporting chemical tanks in the Dyeing Shed | Remove chemical tanks in the area identified above | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this dyeing building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to remove chemical tanks. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement necessary remedial works if required. Chemical tanks were still in place. On 16-Feb-2020: Factory had produced DEA report for the dyeing shed, which was accepted from ACCORD on 12th February 2020, During inspection, water tank was found removed. On 02-Feb-2021: This issue was corrected from previous inspection. Factory had produced Capacity check of slab supporting chemical tanks for the Auto Dispensein of dyeing shed, which was accepted from ACCORD on 12th February 2020, As per DEA recommendation retrofitting work of Auto Dispense was found completed. Also water tank was found removed. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: DEA was accepted from ACCORD on 12th February 2020. Factory has completed all the required remediation. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. DEA was accepted from ACCORD on 12th February 2020. Factory has completed all the required remediation. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. Tank removed. (See CAP-item-54). | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 37 | New Findings-18: Stability and capacity check of steel racks in Building 1 | Factory Engineer to review capacity, loads, connection and related elements of steel racks to confirm stability and capacity for these items | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building-1 which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to check the stability & capacity of the steel racks. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement accepted load plan limit for racks. On 16-Feb-2020: DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, no steel rack was found in building-1. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: No steel racks were found in building-1. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. During inspection, no steel rack was found in building-1. On 03-Apr-2023: This issue was corrected from previous inspection. During inspection, no steel rack was found in building-1. On 5-Jan-2025: Corrected previously. Factory relocated those steel racks. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 38 | New Findings-19: Stability and capacity check of steel racks in Building 1 | Factory Engineer to state the maximum weight that is allowed per square meter. Suggest that state the value on notice boards on these racks | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: After the acceptance of EA , factory need to state the value ( maximum weight is allowed per square meter) on notice board on these racks. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Factory is required to follow the recommendation for loading as per accepted DEA documents. During inspection, no load notice was found for racks. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement accepted load plan limit for racks. On 16-Feb-2020: DEA of Building-1 Four-Storied Building (Proposed Six-Storied) has produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. After completion of retrofitting factory is required to follow the accepted final load plan. During inspection, some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: This issue has been covered in DEA. No load plan was posted on Building-1. Factory is required to post and maintain accepted load plan. On 02-Jan-2022: Load plans were found pasted in each floor. Floor loading was found below the allowable limit of final load plan. However, extension works were found on going as factory got DEA acceptance considering vertical extension up to 5th floor. After completing the extension work, factory is required to follow and post the load plans accordingly. On 06-Sep-2022: Racks have been removed from Building-1. During inspection, no steel rack was found in building-1. On 03-Apr-2023: This issue was corrected from previous inspection. During inspection, no steel rack was found in building-1. On 5-Jan-2025: Corrected previously. Factory relocated those steel racks. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 39 | New Findings-20: Stability and capacity check of steel racks in Building 1 | Maintain standards of quality control to ensure that storage procedures are correctly followed so that overloading problems do not arise in the future | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building-3 which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: After the acceptance of EA , factory need to state the value ( maximum weight is allowed per square meter) on notice board on these racks. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Factory is required to follow the recommendation for loading as per accepted DEA documents. During inspection, no load notice was found for racks. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. After DEA acceptance factory is required to implement accepted load plan limit for racks. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. The factory had commenced retrofitting work but could not continue. During inspection no retrofitting was found on going. After completion of retrofitting factory is required to follow the accepted final load plan. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. After completion of retrofitting factory is required to follow the accepted final load plan. During inspection, some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: No load plan was posted on Building-1. Factory is required to post and maintain accepted load plan. On 02-Jan-2022: Load plans were found pasted in each floor. Floor loading was found below the allowable limit of final load plan. However, extension works were found on going as factory got DEA acceptance considering vertical extension up to 5th floor. After completing the extension work, factory is required to follow and post the load plans accordingly. On 06-Sep-2022: Racks have been removed from Building-1. During inspection, no steel rack was found in building-1. On 03-Apr-2023: This issue was corrected from previous inspection. During inspection, no steel rack was found in building-1. On 5-Jan-2025: Corrected previously. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 40 | New Findings-21: Stability and capacity of the staircase roof at Building 1 | Factory Engineer to review design, loads, roofs and related elements to confirm suitability | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building-1 which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to check the stability & capacity of the staircase at roof. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. After completion of retrofitting factory is required to follow the accepted final load plan. During inspection, some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: Factory submitted DEA and got acceptance for proposed 6 story building. Currently the building in 4 storied. retrofitting is completed for proposed 6 story. On 02-Jan-2022: Factory submitted DEA and got acceptance for proposed 6 story building. Extension works were found ongoing. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Stair roof has been replaced with RCC slab. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. Stair roof has been replaced with RC slab. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 41 | New Findings-22: Stability and capacity of the staircase roof at Building 1 | Replace with appropriate permanent structural elements | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to check the stability & capacity of the staircase at roof. This issue will be covered in DEA. On 31/12/2017: This issue is required to be covered in EA. Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: Remedial works have been suggested with EA reports. The factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection, EA was not submitted to Accord. The factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. During inspection, some mismatch was found in as built drawing of building-1. Factory is required to revised the documents as per verification report and submit to RSC within 10 days after receiving the report. On 13-Sep-2021: Factory has replaced the stair roof with RCC slab. On 02-Jan-2022: Stair roof has been replaced with RCC slab. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. Stair roof has been replaced with RCC slab. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. Stair roof has been replaced with RC slab. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 42 | New Findings-23 :Overall stability system | An Engineering Assessment of the overall building to be carried out and in particular, stability and foundation aspects should be investigated in detail | Corrected | Jan 14 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. This issue will be covered in DEA. On 31/12/2017: Factory has submitted the revised EA report to Accord on 5 Dec 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per EA verification report and submit within mentioned time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of factory building-1 has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) and Dyeing Shed has produced and accepted from ACCORD . During inspection, some mismatch was found in column size of dyeing shed, Factory is required to revised the documents and submit to ACCORD within given timeline. During inspection, building-1 was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. The factory had commenced retrofitting work but could not continue. During inspection no retrofitting was found on going and retrofitting of Dyeing Shed has not started yet, where remediation timeline for dying shed is 15th April 2020. On 02-Feb-2021: DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. Also, revised the EA report for the dyeing shed and Aop shed, which was re-accepted from ACCORD on 22th May 2020. As per EA recommendation some retrofitting is required for Dyeing shed. During inspection, retrofitting work has not started yet, where remediation timeline is 15th July 2020. On 13-Sep-2021: Factory submitted DEA and got acceptance for proposed 6 story building. Currently the building in 4 storied. retrofitting is completed for proposed 6 story. On 02-Jan-2022: Factory submitted DEA and got acceptance for proposed 6 story building. Extension works were found ongoing. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 43 | New Findings-24: Distress due to water ingress in Building 1 | Factory Engineer to inspect water damaged structures and repair with a suitable methods | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to take proper action regarding water ingress as per recommendation. On 31/12/2017: No action has been taken regarding this issue. Factory is required to take proper action regarding water ingress as per recommendation. On 16/07/2018: No action has been taken regarding this issue. Factory is required to investigate the reason of water ingress on roof and repair with suitable method. On 13/12/2018: During inspection, water damaged structure was found. Till date of inspection, factory did take any action to solve this issue. On 04-Jul-2019: During inspection, signs of water ingress were observed. Factory is required to repair the damaged portion and take necessary steps to prevent water ingress. On 16-Feb-2020: No action has been taken regarding this issue. During inspection, building was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: Factory had repaired water damage portion of building-1. On 13-Sep-2021: This issue was corrected in previous follow-up inspection. No water ingress was found. On 02-Jan-2022: No water ingress was found. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. No water ingress was found. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. No water ingress was found. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 44 | New Findings-25: Distress due to water ingress in Building 1 | Waterproofing on the roof slab is to be applied. Moreover the roof slab drainage system should be investigated and improved | In Progress | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to take proper action regarding water ingress as per recommendation. On 31/12/2017: No action has been taken regarding this issue. Factory is required to take proper action regarding water ingress as per recommendation. On 16/07/2018: No action has been taken regarding this issue. Factory is required to investigate the reason of water ingress on roof and repair with suitable method. On 13/12/2018: Till date of inspection, factory did not construct water proofing layer. During inspection, water ponding was found at roof. Factory is required to construct water proofing layer and develop proper drainage system. On 04-Jul-2019: Water proofing layer was not applied. Factory is required to apply water proofing layer and install proper drainage system on rooftops. On 16-Feb-2020: No action has been taken regarding this issue. During inspection, building was found fully evacuated. However verification could not be conducted for Building-1 as the entrance of the both stair of the building was restricted. On 02-Feb-2021: Factory had repaired water damage portion of building-1. DEA of Proposed 6 storied Building 1 ( the existing building is 4 storied) has been produced and accepted from ACCORD on 15th September 2019. During inspection, building-1 was found fully evacuated. During inspection, retrofitting was found on going and roof deck slab was found partially demolished. After completion of demolition work of roof slab, factory is required to provide the proper drainage system with waterproofing membrane. On 13-Sep-2021: Drainage system and waterproofing was not found on rooftop. Factory is required to apply drainage system and waterproofing on rooftop. On 02-Jan-2022: As factory is currently working on the vertical extension, factory will be planning for the drainage system at roof top after the completion of extension work. However, no water ponding was found at roof top. On 06-Sep-2022: Extension works were found on going as per accepted DEA. After completing the extension work, factory is required to apply drainage system and waterproofing on rooftop. On 03-Apr-2023: As per DEA vertical extension works were found on going as per accepted DEA. After completing the extension work, factory is required to apply drainage system and waterproofing on rooftop. On 5-Jan-2025: Water proofing has not been provided. After completing the vertical extension work, factory is required to apply drainage system and waterproofing on rooftop. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | Priority 3 (within 6-months) | In Progress
Follow Up Inspection |  | 45 | New Findings-26: Inadequate stair handrails at Building 1 | Factory Engineer to inspect inadequate items in the area identified above and repair with a suitable methods | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to take action on hand rail as per DEA recommendation. On 31/12/2017: No action has been taken regarding this issue. Factory is required to take action on hand rail as per DEA recommendation. On 16/07/2018: No necessary action has been taken regarding this issue. Factory is required to repair inadequate handrails with a suitable methods. On 13/12/2018: During inspection, distorted handrail was found. Factory is required to take necessary steps to solve this issue. On 04-Jul-2019: Factory has repaired the handrails. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 46 | New Findings-27: Reinforcement left exposed at top level of connection link | For both durability and serviceability, rust proof paint or any appropriate methods is recommended | Corrected | Jun 3 2018 | On 03-12-17: HR Textile is occupied this building which is not covered in ACCORD provided report. But another initial inspected report was found which was conducted by WSP. ACCORD is now recommending to follow the required actions. Factory is required to take action against exposed rebar at roof level of connection level as per DEA recommendation. On 31/12/2017: No action has been taken regarding this issue. Factory is required to take action against exposed rebar at roof level of connection level as per DEA recommendation. On 16/07/2018: The factory has repaired corrosion of exposed rebar by rust proof paint. On 13/12/2018: This issue was corrected from previous inspection. On 04-Jul-2019: Corrected previously. On 16-Feb-2020: This issue was corrected from previous inspection. On 02-Feb-2021: This issue was corrected from previous inspection. Connection link was found demolished. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 3 (within 6-months) | Corrected
Follow Up Inspection |  | 47 | New Findings-28: Three storied RCC building was found adjacent to Building 2. | Factory Engineer to review as built drawing, design, loads, roofs and related elements to confirm suitability | Corrected | Jun 4 2018 | On 03-12-17: Factory engineer is required to survey the as built drawing & review the design of the buildings and submit to ACCORD. On 31/12/2017: Factory engineer is required to survey the as built drawing & review the design of the buildings and submit to ACCORD within given time-line. On 16/07/2018: This issue is required to be covered in EA. . Factory was submitted revised EA on 10 April 2018 and a review mail was sent from Accord on 07th May 2018, but till the date of inspection EA was not submitted to Accord. Factory is required to submit EA to Accord. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of the factory building has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: Factory has produced DEA for Utility Building, which was accepted from ACCORD on 12th February 2020. During inspection, demolition work between utility building and building-2 was not found as per remedial scheme due to site condition, Factory is required to revise the proposed demolition and separation work scheme and submit to ACCORD within given timeline. On 02-Feb-2021: Factory has produced DEA for Utility Building, which was accepted from ACCORD on 12th February 2020. During inspection, demolition work between utility building and building-2 was found completed as per revised remedial scheme due to site condition. Also retrofitting of utility building was found completed. Material test report was found on site for utility building. On 13-Sep-2021: This issue was corrected from previous inspection. On 02-Jan-2022: Retrofitting of utility building was found completed. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 48 | New findings-29 : Steel shed was found besides building 2. | Factory Engineer to review as built drawing, design, loads, roofs and related elements to confirm suitability | Corrected | Jun 5 2018 | On 03-12-17: Factory engineer is required to survey the as built drawing & review the design of the buildings and submit to ACCORD. On 31/12/2017: Factory engineer is required to survey the as built drawing & review the design of the buildings and submit to ACCORD within given time-line. On 16/07/2018: Factory engineer is required to survey the as built drawing & review the design of the shed buildings and submit to ACCORD immediately otherwise provide consent letter to demolish steel shed beside the building-2. On 13/12/2018: This issue is required to cover in DEA. Revised DEA of the factory building has been submitted to ACCORD on 11/12/2018 which is under review. Any recommendation for remedial works as per accepted DEA documents is required to carry out by factory. On 04-Jul-2019: This issue is required to be covered in DEA. Factory last submitted revised DEA on 11th December 2018 and review comments were sent on 28th May 2019. Factory is required to submit revised DEA to ACCORD. On 16-Feb-2020: Factory has produced DEA for AOP shed, which was accepted from ACCORD on 12th February 2020. During inspection, some mismatch was found in column size, Factory is required to revised the documents and submit to ACCORD within given timeline. As per DEA recommendation, retrofitting work is required. Retrofitting has not started yet, where remediation timeline is 15th April 2020. On 02-Feb-2021: Factory has revised the EA report for the AOP shed, which was re-accepted from ACCORD on 22th May 2020. As per EA recommendation some retrofitting is required for AOP shed. During inspection, retrofitting work has not started yet, where remediation timeline is 15th July 2020. On 13-Sep-2021: As per accepted EA, retrofitting work for AOP shed was completed. On 02-Jan-2022: Retrofitting work of AOP shed was completed. Issue remains corrected On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | Priority 2 (within 6-weeks) | Corrected
Follow Up Inspection |  | 49 | New Findings-30: Reinforcement left exposed at top level of Building-2 | For both durability and serviceability, rust proof paint or any appropriate methods is recommended | Corrected | Mar 16 2021 | On 02-Feb-2021: Factory is required to take action against exposed rebar of newly constructed column at roof level of building-2. On 13-Sep-2021: No action has been taken regarding this issue. Factory is required to remove corrosion and apply rust proof coating to the rooftop exposed reinforcement. On 02-Jan-2022: Rust proof paint has been applied at exposed rebar. On 06-Sep-2022: Corrected in the previous inspection. Rust proof paint has been applied to the exposed rebar. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 50 | New Findings-31: Falling hazard on under constructional floors of Building-1. | Install barrier to prevent falling hazard. | Corrected | Oct 21 2021 | On 13-Sep-2021: Falling hazard on under constructional roof floor of Building-1. Install barrier to prevent falling hazard. On 02-Jan-2022: Factory has provided barrier to avoid falling hazard. Issue remains corrected. On 06-Sep-2022: Corrected in the previous inspection. On 03-Apr-2023: This issue was corrected from previous inspection. On 5-Jan-2025: Corrected previously. Parapet was found. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 51 | New Findings-32: Dampness at Building-2 toilet area | Building Engineer is to investigate the reason of the dampness and repair as per advised method | In Progress | Feb 13 2022 | On 02-Jan-2022: During inspection, water leakage was found at toilet block at 3rd floor in building-2. Due to the leakage of water sign of dampness was found on structural member (Column/beam/slab) in the toilet zone. Factory is required to prepared an investigation report of the dampness and repair the affected area properly. Factory management is required to keep the investigation report onsite for further verification. On 06-Sep-2022: Factory has demolished some toilet zone for avoiding the dampness. During the inspection, demolition work was found ongoing. However, no investigation work was found on site. On 03-Apr-2023: During inspection dampness was found several are of building 2. Factory is required to prepared an investigation report of the dampness and repair the affected area properly. Factory management is required to keep the investigation report onsite for further verification. On 5-Jan-2025: Dampness was found at several locations and no investigation report was available on site. Prepare an investigation report and repair the dampness accordingly. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 52 | New Findings-33: Brick wall crack found on facad wall of Building-2. | Building Engineer is to investigate the reason of the crack and repair as per advised method. | In Progress | May 22 2023 | On 03-Apr-2023: During inspection, brick wall crack found on façade wall of building 2. Building Engineer is to investigate the reason of the crack and repair as per advised method. On 5-Jan-2025: During inspection, the crack was found on the brick wall at several locations. The building engineer to repair the crack with a suitable method. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 53 | New Findings-34: Column susceptive to trolley impact. | The Building engineer is required to provide proper barrier around the columns to protect from possible trolley impact. | In Progress | Oct 10 2023 | On 03-Apr-2023: During inspection, damage column found due to trolley impact. The Building engineer is required to provide proper barrier around the columns to protect from possible trolley impact. On 5-Jan-2025: Plaster damage due to trolley impact was found at several places of ground floor of Building-1 and Building-2. Repair damaged plaster and provide column guard. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 months) | In Progress
Follow Up Inspection |  | 54 | New Findings-35: Capacity check of slab supporting chemical tanks in the Dyeing Shed.( Re-Open: Item no. 35 & 36) | Factory Engineer to review design, loads and related elements in area identified above to confirm capacity for these items | We have removed those tanks from roof top | May 22 2023 | On 03-Apr-2023: During inspection, 7 nos plastic water tank was found on the top slab of mezzanine floor of Dyeing shed. Building engineer is required to check the capacity of slab and submit to RSC for review. Previously factory had removed all the plastic water tank from the roof slab of mezzanine. On 5-Jan-2025: Factory has removed all plastic water tanks. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 55 | New Findings-36: Broken tiles found at stair of Building-3. | Building engineer is required to investigate the reason of broken tiles and provide remedial measure. | In Progress | May 22 2023 | On 03-Apr-2023: During inspection broken tiles was found at stair slab of Building-3. Building engineer is required to investigate the reason of broken tiles and provide remedial measure. On 5-Jan-2025: Broken tiles were observed at several places. The building engineer is required to repair/replace the broken tiles. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 56 | New Findings-37: Column of new lift core appeared to be resting on foundation of Building-1. | The building engineer is required to investigate the foundation of the new lift whether it is contributing load on Building-1 or not. If the new lift contributes load on the foundation of Building-1, revise the adequacy of the concerned foundation and submit the documents to RSC for review. | In Progress | Feb 18 2025 | On 5-Jan-2025: During inspection column of the new lift core appeared to be resting on the foundation of Building-1. The building engineer is required to investigate the foundation of the new lift whether it is contributing load on Building-1 or not. If the new lift contributes load on the foundation of Building-1, revise the adequacy of the concerned foundation and submit the documents to RSC for review. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 57 | New Findings-38: Undocumented toilet area with built up at the north side of every floor Building-1. | Remove the built-up and replace the new toilet wall with a lightweight partition. | In Progress | Feb 18 2025 | On 5-Jan-2025: During the inspection, an undocumented toilet area with built-up was found on the north side of every floor of Building-1. Remove the built-up and replace the new toilet wall with a lightweight partition. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 58 | New Findings-39: Non-structural storage racks found not anchored/braced. | Anchor/brace non-structural storage racks. | In Progress | Feb 18 2025 | On 5-Jan-2025: During inspection non-structural storage racks were found not anchored/braced. Anchor/brace non-structural storage racks. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 59 | New Findings-40: Undesignated storage on 3rd floor (Building-2). | Remove all storage from the 3rd floor. Also, implement the accepted load plan. | In Progress | Feb 18 2025 | On 5-Jan-2025: During inspection undesignated storage was found on 3rd floor (Building-2). Remove all storage from the 3rd floor. Also, implement the accepted load plan. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 60 | New Findings-41: Falling hazard at Mezzanine floor (Dyeing Shed). | Provide edge protection/cover the slab opening to avoid falling hazard. | In Progress | Feb 18 2025 | On 5-Jan-2025: During inspection slab opening was found at Mezzanine floor of Dyeing Shed. Provide edge protection/cover the slab opening to avoid falling hazard. RPO Comments on 25-Mar-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | (within 6 weeks) | In Progress

## Fire
Date
01-Sep-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HR TEXTILE/FASHION KNIT, 4 Karnapara, Savar, Dhaka,, Dhaka
Date of Inspection |  | 2014-07-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from work areas, and other spaces on each floor by firerated construction. This was reflected throughout the building on all floors. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | Corrected | Apr 30 2016 | On 26/02/2017: Corrected. (If factory wants to keep the fire rated door open they shall install magnetic door holder ) On 30/5/17: Issue has been reopened on point 18 On 27/08/2017: See point 18. On 05/03/2020: See point 18. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected based on the previous FUI. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage on the first and second floors are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Jan 25 2016 | On 06/12/2016: Corrected. Remarkable storage area has not been found during follow up inspection. On 26/02/2017: Corrected. Remarkable storage area has not been found during follow up inspection. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 05/03/2020: Corrected as per previous follow up. Note: In some places combustible storage found which need to maintain as per standard. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 3 | Storage rooms used for combustible storage on the ground floor are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Jan 25 2016 | On 06/12/2016: Corrected. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in each exit stair enclosure on each floor. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | Corrected | Dec 24 2014 | On 29/09/2016: Corrected. On 06/12/2016: Corrected as per previous follow up. This issue will reflect by the issue no 18. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 16/07/2018: Corrected as per previous follow-up. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 5 | Hazardous materials / flammable liquid storage area located on the ground floor is not separated by fire-rated construction openings, non-rated doors and penetrations. | Separate the hazardous materials / flammable liquid storage room by a minimum 2- hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | Jan 19 2016 | On 29/09/2016: Corrected. On 06/12/2016: Corrected. Relocated. On 26/02/2017: Corrected. On 30/5/17: Corrected. Removed. On 27/08/2017: Corrected. Removed. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 6 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes, and exit discharge. This was reflected throughout the building on all floors. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Dec 24 2014 | On 29/09/2016: Corrected. On 06/12/2016: Corrected. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 10/12/2017: Corrected. On 16/07/2018: Corrected. On 07-05-2019: Corrected on previous follow-ups. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Immediate | Corrected
Initial Inspection |  | 7 | Storage areas were located in all exit stairwells on the ground floor, underneath the stairs, and all floors above. | Remove all storage from exit stairs and egress paths. | Corrected | Jan 19 2016 | On 29/09/2016: Corrected. On 06/12/2016: Corrected. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 05/03/2020: Corrected as per previous follow up. Note: A single water pump has been found in underneath the staircase in ground floor which need to remove from here or keep as per standard. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Storage within egress paths were present on the first and second floors. | Keep egress paths and stairs clear of storage. | Corrected | Dec 24 2014 | On 29/09/2016: Corrected. On 06/12/2016: Corrected. Egress paths has been found free from storage. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Immediate | Corrected
Initial Inspection |  | 9 | Collapsible gates / sliding doors are provided at building exits, exit stairs, along egress routes, and exit discharge. This was reflected throughout the building on all floors. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Dec 24 2014 | On 30/5/17: Corrected. On 27/08/2017: Corrected. On 10/12/2017: Corrected. On 16/07/2018: Corrected. On 07-05-2019: Corrected on previous follow-ups. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 1 month | Corrected
Initial Inspection |  | 10 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | We had replaced the fire alarm system with listed addressable system and were preapring for T&C. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Jul 30 2016 | On 05/03/2020: Installation has been completed. Factory person said that they will apply for T&C to the Accord in next week. On 13-Sep-2021: Installation work is on-going. On 02/01/2022: The installation has been completed. The factory has been submitted the drawing and necessary documents to the RSC on 31/12/2021 for pre-T&C review. RPO Comments: On 27-May-2024 as per the factory's requested email, the RSC observed that the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) systems are presently not ready for Pre testing & commissioning. The RSC has changed the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) status on “ongoing” and change the Corrective action plan item on “In progress”. The factory is required to submit the as-built documents for review after work completion, so that the RSC may proceed for T&C or further steps. On 15-Sep-24: Due to road construction (public road) and retrofitting work, some modification was required in the system which is on going. Reportedly, after completing the modification work, documents for T&C will be submitted to RSC by 1st week of Dec,2024. RPO Comments: On 31-Aug-2025,the RSC postponed the Pre-testing and commissioning inspection for 2nd June 2024, based on the factory's request that the systems were not ready. The submission of as-built documents is required upon completion of the work. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 11 | Inspection, testing, and maintenance records for the fire alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | We had replaced the fire alarm system with listed addressable system and were preapring for T&C. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Jul 30 2016 | On 27/08/2017: It is an integrated part of automatic fire alarm system. On 10/12/2017: It is an integrated part of fire alarm system. On 16/07/2018: No action has been taken yet. On 07-05-2019: Integral part of FA system. On 05/03/2020: It is an integrated part of fire alarm system. On 13-Sep-2021: Integrated part of FA system. On 02/01/2022: The installation has been completed. The factory has been submitted the drawing and necessary documents to the RSC on 31/12/2021 for pre-T&C review. RPO Comments: On 27-May-2024 as per the factory's requested email, the RSC observed that the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) systems are presently not ready for Pre testing & commissioning. The RSC has changed the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) status on “ongoing” and change the Corrective action plan item on “In progress”. The factory is required to submit the as-built documents for review after work completion, so that the RSC may proceed for T&C or further steps. On 15-Sep-24: It is an integrated part of fire alarm system. RPO Comments: On 31-Aug-2025,the RSC postponed the Pre-testing and commissioning inspection for 2nd June 2024, based on the factory's confirmation that the systems were not ready. The submission of as-built documents is required upon completion of the work. | Within 3 months | In Progress
Initial Inspection |  | 12 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants | Replace the single-station smoke alarms. Provide automatic smoke detection throughout the building in accordance with NFPA 72. | Corrected | Jul 30 2016 | On 16/07/2018: It is an integrated part of fire alarm system. On 07-05-2019: Integral part of FA system. On 05/03/2020: Corrected. Factory has been installed the automatic fire alarm & detection system & remove all single station smoke alarms. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected based on previous FUI. On 15-Sep-24: Corrected | Within 6 months | Corrected
Initial Inspection |  | 13 | Manual on-off switch is provided for emergency lighting units. This was reflected throughout the building in various locations. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | Dec 24 2014 | On 30/5/17: Corrected. On 27/08/2017: Corrected. On 10/12/2017: Corrected. On 16/07/2018: Corrected. On 07-05-2019: Corrected on previous follow-ups. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 1 month | Corrected
Initial Inspection |  | 14 | Exit signage not illuminated (burned out, broken, etc.). This was reflected throughout the building on various floors. | Regularly inspect all exit signage and replace/install lights as needed to illuminate signs. | Corrected | Jan 19 2016 | On 30/5/17: Corrected. On 27/08/2017: Corrected. On 10/12/2017: Corrected. On 16/07/2018: Corrected. On 07-05-2019: Corrected on previous follow-ups. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 1 month | Corrected
Initial Inspection |  | 15 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. This was reflected throughout the building on all floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Feb 20 2016 | On 29/09/2016: Corrected. On 06/12/2016: Corrected. It is required to increase emergency lights on some floors specially at cutting floors and ground floor. On 26/02/2017: Corrected. On 30/5/17: Corrected. On 27/08/2017: Corrected. On 05/03/2020: Corrected as per previous follow up. Note: Factory need to re-arrange some position of emergency light as per standard for fulfil the required lux. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Jan 19 2016 | On 30/5/17: Corrected. On 27/08/2017: Corrected. On 10/12/2017: Corrected. On 16/07/2018: Corrected as per previous follow-up. Factory was unable to show any document regarding this. On 07-05-2019: Corrected on previous follow-ups. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected | Within 3 months | Corrected
Follow Up Inspection |  | 17 | New Finding: The existing high-rise building with an occupiable floor greater than 23 m (75 ft) above the finished grade is not protected with an approved automatic sprinkler system. The large occupant loads, heavy fuel loading, and anticipated extended egress times warrant sprinkler protection. | Provide an automatic sprinkler protection throughout the building in accordance with NFPA 13. | We had installed the sprikler system and were preapring for T&C. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Aug 30 2016 | On 07-05-2019: Work in progress. On 05/03/2020: Installation has been completed. Factory person said that they will apply for T&C to the Accord in next week. On 13-Sep-2021: Installation and/or modification work is on-going. On 02/01/2022: The installation has been completed. The factory has been submitted the drawing and necessary documents to the RSC on 31/12/2021 for pre-T&C review. RPO Comments: On 27-May-2024 as per the factory's requested email, the RSC observed that the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) systems are presently not ready for Pre testing & commissioning. The RSC has changed the Fire Alarm & Detection System (FADS) & Fire Suppression System (standpipe & hose, sprinklers) (SUPS) status on “ongoing” and change the Corrective action plan item on “In progress”. The factory is required to submit the as-built documents for review after work completion, so that the RSC may proceed for T&C or further steps. On 15-Sep-24: Due to road construction (public road) and retrofitting work, some modification was required in the system which is on going. Reportedly, after completing the modification work, documents for T&C will be submitted to RSC by 1st week of Dec,2024. RPO Comments: On 31-Aug-2025,the RSC postponed the Pre-testing and commissioning inspection for 2nd June 2024, based on the factory's confirmation that the systems were not ready. The submission of as-built documents is required upon completion of the work. | Installation within 4 months | In Progress
Follow Up Inspection |  | 18 | New Finding (6th follow up): The exit stairs are not separated from work areas, and other spaces on each floor by firerated construction. This was reflected throughout the building on all floors. (Factory has installed fire doors, some doors damage, some door hold open devices missing, door hold open devices coonection is not proper way, openings and pentrations are available at stairs) | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | Exit statis will be separated. We had replaced the fire alarm system with listed addressable system and were preapring for T&C. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Jan 5 2017 | On 05/03/2020: Factory has been installed fire rated door in all exit with magnetic door holder. Few doors are not closing properly due to door coordinator. On 13-Sep-2021: Not Corrected. Fire doors were found damaged, with excessive clearance and kept open by door wedges. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Issue re-opened. Newly vertically extended 4th floor was under construction where temporary dining, prayer and storage areas were found during inspection. Stair was not separated in the 4th floor. RPO Comments on 31-Aug-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 19 | New Finding (On 10/12/2017): Heavy fire load has been observed at the production floors due to the presence of large area of unenclosed combustible storages. | Provide defined storage areas and limit the storage arrangement as Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | Jan 10 2018 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Remedial action has not been completed yet. Additionally storage has been observed under cutting table. On 05/03/2020: Factory has been organized in process storage as per standard in some area but in few area still now need to organized. On 13-Sep-2021: Not corrected. In-process storage were found without proper maintenance as per the recommendation. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Corrected | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New Finding (On 10/12/2017): During the inspection egress aisles were obstructed by combustible storages and available clear width were found less than 36 inch. | Provide aisles free from obstructions and with minimum clear widths of 36-inch. | Corrected | Dec 20 2017 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Not Corrected yet. On 05/03/2020: Corrected. On 13-Sep-2021: Issue reopened. At few areas, aisles were found obstructed. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 21 | New Finding (On 10/12/2017): Storage was located in the exit stair. | Remove all storage from exit stairs. | Corrected | Dec 20 2017 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Obstruction by construction material was observed at exit stair. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 22 | New Finding (On 10/12/2017): The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Corrected | Dec 20 2017 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Remedial work has not been completed yet. On 05/03/2020: Corrected. On 13-Sep-2021: Issue reopened. Egress path were blocked by storages. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 23 | New Finding (On 10/12/2017): Exit stair(s) is discharge the occupants inside the building. | 1. Modify stair to discharge directly outside. Or 2. Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). Or 3. Provide sprinkler protection for discharge floor in accordance with NFPA 13. | Corrected | Jan 10 2018 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Remedial work has not been completed yet. On 05/03/2020: Corrected. Factory has been demolish the required portion of building to reach the standard. On 13-Sep-2021: Issue reopened. Exit stair from RCC building discharge occupants in the connected dyeing Shed at ground floor. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New Finding (On 10/12/2017): Chemical storage area is not separated by fire-rated construction having non rated door and unsealed penetrations and openings. | Separate the chemical storage room by 2-hr fire rated construction. Seal all penetrations and protect the openings to maintain the required fire separations. Keep 16-points MSDS of all chemicals in the storage area. | Corrected | Jan 10 2018 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Corrected. Removed. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New Finding (On 10/12/2017): A single means of exit has been provided. Officers/Staff dinning room. | Maintain maximum 30 occupants having a travel distance of 23m (75 ft). Or Provide additional exit. | Corrected | Dec 20 2017 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. Note: Dining separation is required. On 07-05-2019: Although corrected for mentioned location, Due to retrofitting work in main building one of the available two stair is inaccessible and current occupant load (more than 300) does not meet standard. On 05/03/2020: Corrected. Retrofitting at stair portion almost completed & a temporary but adequate steel stair is provided from 1st floor to ensure uninterrupted exit discharge. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 26 | New Finding (On 10/12/2017): Exit capacity is not adequate for the occupant load. (Modular Part)/ Exit Capacity- 325/Observed occupants-400 | 1. Reduce occupant load to not more than available exit capacity. Or 2. Provide additional exits to increase exit capacity. | Corrected | Dec 20 2017 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Although it has been reduced, Due to retrofitting work in main building one of the available two stair is inaccessible and current occupant load does not meet standard. On 05/03/2020: Corrected. Retrofitting at stair portion almost completed & a temporary but adequate steel stair is provided from 1st floor to ensure uninterrupted exit discharge. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 27 | New Finding (On 10/12/2017): Based on observation emergency lights were found insufficient in few places. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Jan 10 2018 | On 10/12/2017: New Finding On 16/07/2018: Partially corrected. On 07-05-2019: Not completed yet. On 05/03/2020: Partially corrected. Factory has been increased emergency light which photo has been sent to the Accord after inspection. Its need to physically verified by the Accord. On 13-Sep-2021: Still modification required at some floors. Top floor of second building is not provided with EL. On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding (On 10/12/2017): Finish goods storage room were observed without any fire separation from adjacent production floors. | Rooms used for storage of combustible materials are not separated from the surrounding occupancy/areas | we will install fire separation as soon as factory is functional. | Jan 10 2018 | On 10/12/2017: New Finding On 16/07/2018: No action has been taken yet. On 07-05-2019: Remedial work has not been completed yet. On 05/03/2020: Corrected. On 13-Sep-2021: Issue reopened. Found without any fire separation. (Note: Fire rated assembly might be removed due to retrofitting work). On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Issue reopened. AOP shed (accessories & carton store shed) was not separated from production occupancy (sample dyeing shed). RPO Comments on 31-Aug-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 29 | New Finding in 11th Follow-up: Boiler and generator room is not separated by fire rated construction (openings, non-rated doors, penetrations). Location: Ground floor building-2 | Separate the generator and boiler room by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain fire separations. | Corrected | Aug 16 2018 | On 16/07/2018: New Finding On 07-05-2019: Corrected. Fire door has been provided. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 30 | New Finding in 11th Follow-up: Unsealed penetrations and openings are located in the exit stair enclosures | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separations. | Corrected | Aug 16 2018 | On 16/07/2018: New Finding On 07-05-2019: Remedial action has not been completed yet. Due to retrofitting work several penetrations were observed in exit stair enclosure. On 05/03/2020: Corrected. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding in 11th Follow-up: Tripping hazards were found on the doors during the time of inspection. | Revise main entrance do there is no lip or other protrusion that may cause tripping. Changes in elevation of walking surfaces do not exceed 6.35 mm (1/4 in) unless provided with a bevelled slope of 1 in 2 that does not exceed 12.7 mm (1/2 in). | Corrected | Jul 23 2018 | On 16/07/2018: New Finding On 07-05-2019: Remedial action has not been completed yet. On 05/03/2020: Corrected. Remediation work has been completed. On 13-Sep-2021: Corrected on previous follow-ups. On 02/01/2022: Corrected. On 15-Sep-24: Corrected. | Within 1 week | Corrected
Follow Up Inspection |  | 32 | New Finding (14th FU): The Open side of the exit stair is a falling hazard. And it is only protected by a handrail of 34 inch. | Provide additional edge protection with a minimum height of 1067mm (42 inch.). | Completed | Oct 13 2021 | On 13-Sep-2021: New Finding, On 02/01/2022: Corrected based on the site observations. On 15-Sep-24: Issue re-opened. Newly vertically extended 4th floor, construction work is on going and guard rail was found less than 42 inch which can cause a falling hazard. RPO Comments: On 25-Mar-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 33 | New Finding (16th FU): A single means of exit has been found on AOP shed (accessories & carton store shed) and discharged through production occupancy (sample dyeing shed) where travel distance exceed 30m. | Maintain maximum 30 occupants having a travel distance of 30m (100 ft). Or Provide additional exit. | we have ensured additiona exit | Oct 30 2024 | On 15-Sep-24: New Finding RPO Comments: On 2-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 34 | New Finding (16th FU): Unsealed penetrations are located in the fire rated floor/ceiling assemblies due to pvc utility pipe. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's guideline (Type-1 Construction). or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required (Type-1 Construction). | All penteration will be sealed properely as soon as the factory is functional. | Dec 30 2024 | On 15-Sep-24: New Finding RPO Comments on 31-Aug-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress

## Electrical
Date
01-Sep-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | HR TEXTILE/FASHION KNIT, 4 Karnapara, Savar, Dhaka,, Dhaka
Date of Inspection |  | 2014-07-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Burnt sign found in transformer. | The damaged transformer needs to be removed and replaced with new one. Contact REB supplier to take necessary action. | Corrected | Apr 30 2015 | On 18/08/2015: Corrected. | 1 Month. | Corrected
Initial Inspection |  | 2 | Generator output Cable laid on concrete floor. | Lay the cable inside cable trench/Install cable duct to protect the generator output cables and provide covers made of non combustible material preferably metal to protect the cables insulation from any physical damage. | Corrected | Dec 24 2014 | On 19/01/2016: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Control device mounted on wall without enclosures. | MCCB (electrical devices) mounted on the wall must be installed with protective metallic enclosures of minimum 20 SWG thickness. | Corrected | Apr 30 2015 | On 18/08/2015: Corrected. | 1 Month. | Corrected
Initial Inspection |  | 4 | Power and control wiring of motors are carried through flexible PVC pipe. | Use industrial graded (heat resistant) pipe for control and power wiring of motors to prevent cables from damage due to excessive heat or Install cable tray made of non-combustible material preferably metal to support and protect the cables. | Corrected | Apr 30 2015 | On 18/08/2015: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Cables/wires passing through wall not protected and remaining gaps around the cable/wiring not sealed. | Cables/wirings passing through permanent wall must be protected installing pipes and remaining gaps must be sealed with fire resistant materials. Cable tray/ raceway shall be installed for the support of the cable throughout its length. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New timeline: 15/05/16. On 25/07/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | Cables terminating to/from Change Over Switch are not supported. | Cables terminating at Change Over Switch (and other cables) must be supported on ladders/ trays with cover to prevent any physical damages. | Corrected | Apr 30 2015 | On 18/08/2015: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | LT panel without enclosures. | Panel rear body must be enclosed properly with metal enclosure and make circular hole at the base plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. | Corrected | Apr 30 2015 | On 31/03/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 8 | Barrier/separators between different phases are not installed (typical). | Install separators between different phases of MCCB. Standard separators. | Corrected | Apr 30 2015 | On 18/08/2015: Corrected. | 1 Month | Corrected
Initial Inspection |  | 9 | Hot spots detected at terminal of MCCB due to overloading and loose connection. | Inspection is needed to identify exact reason for creating high temperature. In case of overloading; select the power cables by calculating the connected load or in case of loose connection. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New timeline: 15/05/16. On 25/07/2016: Not Corrected. On 29/09/2016: Not Corrected. On 06/12/2016: Not Corrected. On 26/02/2017: Corrected. No hot spot has been found during inspection period. | 1 Month | Corrected
Initial Inspection |  | 10 | Multiple wires installed in single lug/terminal (typical). | Every wire terminating must be installed using individual lug/terminal according to respective cable size to avoid loose connection. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New timeline is till 15/05/16 On 25/07/2016: Not Corrected. On 29/09/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 11 | Cable trench without cover and lint/dust found inside the cable duct. | Clean the dust inside the cable-duct and provide cover (made of non-combustible material) for the cable-duct to prevent the further accumulation of dust inside the duct. Make sure power source of the cables are disconnected before cleaning. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 12 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. | Corrected | May 15 2016 | On 31/03/2016: The mentioned issue is done but still found for others generator. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 13 | New Finding: Generator body has been earthed by inadequate/ improper sized (type) cable. | Ensure minimum two earthing connection for generator body (consult with your generator supplier). | Corrected | May 15 2016 | On 31/03/2016: Still generator body and neutral has been earthed by inadequate ECC. New committed timeline is given till 15/05/2016. On 25/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 14 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has of no use. | Replace cable tray by wider one; or use additional cable tray to distribute cables thus 20-25% tray area are kept free (if you cover it). | Corrected | Nov 28 2015 | On 31/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 15 | New Finding: Panel doors are not connected with earth. | All metal panel doors shall have earth connection by at least 4 rm earth cable. | Corrected | Sep 28 2015 | On 18/08/2015: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 16 | New Finding: Distribution Board's top/ bottom is left open (typical issue). | Seal each distribution board's top/bottom; and use cable glands holding/ supporting cables. | Corrected | Nov 28 2015 | On 31/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 17 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs. | Terminate all the power/earth/neutral cable with proper sized cable lug. | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 18 | New Finding: Cables are hanging without support. Cable terminals may be in tension. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 19 | New Finding: Cables in service are joined (splicing) between terminations. | Existing cables with joints must be spliced using butt splicing kits and then should be insulated with electrical tapes. Joints must be supported and protected. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 20 | New Finding: No/Inadequate rubber (insulation) mat on the working are of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries). | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16 On 25/07/2016: Not Corrected. On 29/09/2016: Not Corrected On 06/12/2016: Not Corrected. On 26/02/2017: Not corrected. On 30/05/2017: Not corrected. On 28/08/2017: Not Corrected. On 10/12/2017: Not Corrected. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Not Corrected. They are working on this issue. On 13/09/21: Not Corrected.. Factory is working on it. On 02/01/2022: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: MCCB/MCB is not fixed with base. | Need to fix the MCCB/MCB with the base of the panel. | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Flexible PVC pipe has been used inside the panel to cover cables. | Remove all the flexible PVC pipes from inside of the panel. | Corrected | Oct 28 2015 | On 19/01/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: Cables inside distribution board is disorganized. | Organize all the power cables securely inside distribution board thus no chance of any electrical hazard. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16. On 25/07/2016: Not Corrected. On 29/09/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Cable in store room/storage areas is uncovered. | Cable in store room/storage areas shall be covered/concealed. | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Unterminated wire is kept inside the electrical panel/cable tray. | All unterminated wires shall be removed. | Corrected | Sep 28 2015 | On 31/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Panel/Distribution boxes are not readily accessible. | Take necessary initiative thus every panel/ distribution board can be easily accessible. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16. On 25/07/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Exposed and heated steam line is close to cable channel. | Wires close/attached to steam line/heat source must be protected from external heat. In unavoidable case provide proper insulation for the heat source/steam line or cover the hot water drain. Normally power cable should keep 0.9m apart from hot area. | Corrected | Sep 28 2015 | On 31/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Electrical panel/ distribution board/installations is covered with inflammable materials. | Inflammable materials must be stacked maintaining a safer (1.5 m apart ) clearance from any electrical installation. | Corrected | Sep 20 2015 | On 19/01/2016: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 30 | New Finding: Distribution board/panel is filled with fluffs (lint/dust). | Keep always clean inside all the distribution boards/panels. Seal them properly and ensure adequate ventilation. | Corrected | Sep 28 2015 | On 31/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Cables are hanging without support. | Use cable tray/ladder to support cables at any where to keep cable out of tension. | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 32 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16. On 25/07/2016: Not Corrected. SLD is not as built. On 29/09/2016: Not Corrected. SLD is not as-built On 06/12/2016: Not Corrected. According to factory personnel SLD will be updated after complete renovation. On 26/02/2017: Not corrected. On 30/05/2017: Not corrected. On 28/08/2017: Not Corrected. On 10/12/2017: Not Corrected. SLD is not as built. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Not Corrected. They are working on this issue. On 13/09/21: Not Corrected. i. Drawing is not as-built due to new electrical installation. ii. Equipment identification not completed yet. iii. Breaker set point not adjusted as per SLD. Factory shall be submitted the SLD (new installed electrical system alone with Accepted SLD) to RSC for review. On 02/01/2022: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Lightning Protection System (LPS) drawing is unavailable. | Design LPS as built and share with Accord to get information any necessary modification. | Corrected | May 15 2016 | On 31/03/2016: Actual condition on building and drawing have mismatch information. New committed timeline is till 15/05/16 On 25/07/2016: Not Corrected. On 29/09/2016: Not Corrected. LPS is installed but all metal on roof need to be bonded. On 06/12/2016: Not Corrected. All metals should also be bonded to LPS system. Excess rods should be cut down or bonded. Mesh conductor is not clamped properly at some places. On 26/02/2017: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Insulation resistance test of electrical cables is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Corrected | May 15 2016 | On 31/03/2016: Report is available but not covered all system. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected | Oct 28 2015 | On 31/03/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). | Corrected | Sep 28 2015 | On 19/01/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Earth Continuity Conductor (ECC) in the distribution box is undersized /improper. | Increase ECC size for whole factory according to BNBC 2006 Part 8 Chapter 2 section 2.8 (Usually ECC should be equal to the half of the respective phase cable). | Corrected | May 15 2016 | On 31/03/2016: Most of panel don't have Earthing bus bar and also ECC cable is inadequate. New committed timeline is till 15/05/16 On 25/07/2016: Not Corrected. On 29/09/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Earth connections are not segregated & earth pit are inadequate. | Ensure separate earthing connection for Generator body, transformer body, Electrical system and Lightning Protection System. Mark them all. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16 On 25/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Corrected | May 15 2016 | On 31/03/2016: Not Corrected. New committed timeline is till 15/05/16. On 25/07/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board bus bar using a proper type protection arrangement (MCCB/MCB). | Corrected | Apr 10 2017 | On 30/05/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | Corrected | Nov 10 2017 | On 10/12/2017: Not Corrected. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland. | Corrected | Oct 10 2017 | On 10/12/2017: Not Corrected. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Oct 10 2017 | On 10/12/2017: Not Corrected. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Cables are laid on floor inside cable trench haphazardly. | Cables inside cable trench have to be guided and routed properly. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. | Corrected | Nov 10 2017 | On 10/12/2017: Not Corrected. On 16/07/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Completed. | Oct 10 2017 | On 10/12/2017: Not Corrected. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: MCCB is installed in improper enclosure and live terminal left exposed (closed to metal body). | Each MCCB/MCB must be enclosed properly with base plate and cable gland for cable entry/exit. | Corrected | Dec 30 2017 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 2 Weeks | Corrected
Follow Up Inspection |  | 47 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/ panels is obstacles. | At least 1 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Hazardous lights in store room/storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Not corrected. On 07/05/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: MCCB installed at improper location inside panel board. | MCCB must be installed with easy access from the front of the panel board. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: BBT feeder box is left open (typical issue). | Each feeder box/tap off box must be properly sealed to avoid ingression of fluffs. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Not corrected. On 07/05/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Not corrected. On 07/05/2019: Not Corrected. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Jan 15 2018 | On 10/12/2017: New Finding. On 16/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Cables are hanged outside wall of the building (exposed to the weather) without proper protection. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Corrected | Jul 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Oil spillage/ leakage has been observed in generator room. | Any kind of oil spillage/leakage must be stopped; and generator must be kept always dry. | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Cables are laid on floor inside cable trench haphazardly. | Cables inside cable trench have to be guided and routed properly. A cable tray shall be installed in the trench to ensure proper support and dressing for cables. | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Not Corrected. For retrofitting work, they are not able to start this work. On 13/09/21: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Excess cables coiled and kept unsupported at the back of panel. | Unsupported/unprotected power cables must be supported/protected by cable tray/ladders (If it is HT cable, rearrangement shall be made rather than trimming). | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Not Corrected. For retrofitting work, they are not able to start this work. On 13/09/21: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Cable tray cover creates obstacles around the electrical installations which has trip hazard. | Work place around each electrical installation shall be uniformly leveled. | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Not Corrected. For retrofitting work, they are not able to start this work. On 13/09/21: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | completed. | Jun 15 2019 | On 07/05/2019: New Finding. On 09/02/2021: Not Corrected. For retrofitting work, they are not able to start this work. On 13/09/21: Not Corrected. New electrical system Installation is going on. On 02/01/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Lightning Protection System (LPS) is unavailable for building-01 (Due to building extension). | Design LPS as built and share with Accord to get information any necessary modification. | LPS system has been installed. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Nov 23 2021 | On 13/09/21: New Finding On 02/01/2022: Not Corrected. Building construction is going on. On 20/12/2023: Not Corrected. No progress observed on LPS installing. On 26/05/2024: Not Corrected. Notable progress observed as factory installed LPS, however, exposed metal bonding (rods) was missing. Also construction work is going on at the rooftop. On 05/01/2025: Not corrected. Factory has installed LPS in building 1 but earth pits have been found undersize as per design & metal bonding has not been done. LPS not maintained properly in building 3 (air terminal missing & height issue). Again LPS has not installed & design not found for Store shed (previously AOP shed). RPO Comments on 31-Aug-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 63 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | SLD will be updated. Recently the factory is not operational and floor is empty. We will resume the work as soon as the factory is functional. | Feb 24 2024 | On 26/05/2024: Not Corrected. Progress observed as factory got accepted SLD, however, earthing layout mismatched with SLD, some oversized breakers observed and as-built drawing was not available. On 05/01/2025: Not corrected. Factory has got SLD Accepted again from RSC on September 2024. Some mismatch has been observed in field (cable/CB not marked properly, CB not adjusted, loads are not properly identified, individual overload protection missing/oversize etc) with SLD. RPO Comments on 31-Aug-2025: The factory management is working on it. The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 Months | In Progress
Follow Up Inspection |  | 64 | New Finding: Periodicity of earth Pit resistance test record is not continued. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | completed. | Jan 24 2024 | On 26/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Periodicity of insulation resistance test record is not continued. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | completed. | Jan 24 2024 | On 26/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | completed. | Jan 24 2024 | On 26/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Safety program is initiated but has no influence in the factory all electrical personnel. | Electrical safety training and awareness program for all electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | completed. | Jan 24 2024 | On 26/05/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Uninsulated electrical tools are used by maintenance personnel in the factory. | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. | completed. | Feb 24 2024 | On 26/05/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 69 | New Finding: Hot spots have been observed at one points. (above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Hot sports have been eliminated and daily surveillance is going on. | Jul 1 2024 | RPO Comments: On 22-Sep-2024 the factory management reported the remediation completion. This item will be verified in the next inspection. On 05/01/2025: Corrected. | 1 Month | Corrected