## Structural
Date
04-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ingenitex (BD) Limited, Jamgora , Ashulia, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2023-02-13
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Inconsistences in design report. | Building engineer is required to design, load and flexural capacity of the beams. | Corrected | Apr 12 2023 | On 07-May-2023: This issue is required to be covered under EA. Factory has submitted the EA to RSC which is under review. On 20-Sep-2023: This issue will be covered by Engineering Assessment (EA). Factory is required to submit the EA within 27-Sep-2023 as per the accepted timeline for re-submission. On 17-Oct-2024: This issue has been covered in Engineering Assessment(EA) which was accepted from RSC on 31-Mar-2024. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 2 | Inconsistences in design report. | Building engineer is required to revise the design report as per BNBC 1.9.1 requirements. | Corrected | Apr 12 2023 | On 07-May-2023: This issue is required to be covered under EA. Factory has submitted the EA to RSC which is under review. On 20-Sep-2023: This issue will be covered by Engineering Assessment (EA). Factory is required to submit the EA within 27-Sep-2023 as per the accepted timeline for re-submission. On 17-Oct-2024: This issue has been covered in Engineering Assessment(EA) which was accepted from RSC on 31-Mar-2024. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 3 | Inconsistences in design report. | Carry out remedial works where required | Corrected | Sep 1 2023 | On 07-May-2023: This issue is required to be covered under EA. Factory has submitted the EA to RSC which is under review. Factory is required to carry out the remediation work after acceptance of EA if required. On 20-Sep-2023: This issue will be covered by Engineering Assessment (EA). Factory is required to submit the EA within 27-Sep-2023 as per the accepted timeline for re-submission. After getting EA acceptance from RSC, factory is required to carry out remedial works (if required). On 17-Oct-2024: This issue has been covered in Engineering Assessment(EA) which was accepted from RSC on 31-Mar-2024. As per accepted EA, no remediation was required. On 19-Feb-2026: Previously corrected. | within 6-months | Corrected
Initial Inspection |  | 4 | Discrepancies in as-built drawings. | Building engineer is required to survey the whole structure and prepare accurate as-built drawings. | Corrected | Apr 12 2023 | On 07-May-2023: This issue is required to be covered under EA. Factory has prepared as built drawing as per of EA and submitted them to RSC which is under review. On 20-Sep-2023: This issue will be covered by Engineering Assessment (EA). Factory is required to submit the EA within 27-Sep-2023 as per the accepted timeline for re-submission. On 17-Oct-2024: This issue has been covered in Engineering Assessment(EA) which was accepted from RSC on 31-Mar-2024. During the inspection, as-built drawings were found satisfactory with on-site condition. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 5 | Hairline crack on beams and crack in the brick walls. | Building engineer is required to investigate the reason of crack and repair with suitable method. | Corrected | Apr 12 2023 | On 07-May-2023: Factory has prepared crack investigation report. During inspection, it was observed that factory has completed the repairing works in the crack areas on beams and masonry walls as per the crack investigation report which was found satisfactory. On 20-Sep-2023: Corrected previously. During inspection, a crack investigation report was found on-site where the cracks were declared as non-structural. Factory has repaired the cracks. No further crack was observed at the time of inspection. On 17-Oct-2024: Corrected previously. A crack investigation report was found on-site and the factory has repaired the crack as per investigation report. During Inspection, no further crack was observed on beam and brick walls. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 6 | Anchorage and bracing of storage racks. | Building engineer is required to provide the proper anchorage as per BNBC seismic requirements. | Corrected | Apr 12 2023 | On 07-May-2023: Factory has provided adequate anchorage in storage racks and plastic water tank at roof. On 20-Sep-2023: Corrected previously. During inspection, storage racks and plastic water tanks were found braced & anchored properly. On 17-Oct-2024: Corrected previously. The factory was provided braced on all non- structural elements, including storage racks. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Initial Inspection |  | 7 | Complete the water/heat proofing works on the roof. | Building engineer is required to complete the water/heat proofing works on the remaining part roof. | Corrected | Apr 12 2023 | On 07-May-2023: Factory has not completed the water/heat proofing works in the remaining part of roof. Factory is required to complete the water/heat proofing works. On 20-Sep-2023: Till the date of inspection, no action was taken by factory management regarding this issue. Factory is required to provide the water / heat proofing layer on the roof (remaining part). On 17-Oct-2024: During the inspection, the factory has started the water/heat proofing work on the roof. However, the factory is required to complete the work. On 19-Feb-2026: Factory provided cementitious waterproofing layer. | within 6-weeks | Corrected
Initial Inspection |  | 8 | Inadequate vehicle impact protection system. | Building engineer is required to design and construct a proper vehicle impact protection system around the susceptible columns on ground floor. | Corrected | Apr 12 2023 | On 07-May-2023: Factory has provided vehicle impact protection system using MS angle around the RC columns in ground floor. On 20-Sep-2023: Corrected previously. Factory has provided column safety guard at ground floor which was found adequate. On 17-Oct-2024: Corrected previously. The factory has provided adequate column barrier at ground floor to avoid vehicle impact. On 19-Feb-2026: Previously corrected. | within 6-weeks | Corrected
Follow Up Inspection |  | 9 | New findings: 1 Trolly impact observed at column in several floors. | Building engineer is required to provide safety column guard to protect the column from trolly impact. | Corrected | Nov 7 2023 | On 20-Sep-2023: During inspection, trolly impact was observed at the column in several floors. Building engineer is required to provide the safety column guard to protect the columns from the trolly impact. On 17-Oct-2024: Corrected previously. The factory has provided column guard to avoid trolly impact. On 19-Feb-2026: Previously corrected. | (within 6 weeks) | Corrected

## Fire
Date
04-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ingenitex (BD) Limited, Jamgora , Ashulia, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2023-02-13
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stair enclosures are not separated from [work areas, other spaces] due to penetrations and openings by fire-rated construction. | Separate the exit stairs from work areas and other building spaces on all floor levels by minimum 2- hr fire-rated construction. Provide minimum 1.5- hr fire rated doors and seal all unprotected openings and penetrations to maintain the fire separation. Ensure that all fire doors are self-closing and positive latching, and are provided with fire exit (panic) hardware where serving production floors or assembly occupancies. If fire doors are required to be held open for functional reasons, provide automatic-closing devices tied to the fire alarm system. Once fire doors are installed, every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets RSC Technical Guidelines (Standard) V1- 6.8.3.1. | The facility management has installed and functional, exit stair enclosures properly separated to penetration of compressor room's duct, lift m/c room at stair-2 and Fire door installed the security server room at stair-1. Work Done | Jun 1 2023 | On 20/09/2023: Work in-progress. Fire doors have been installed and found functional, but the exit stair enclosures were not properly separated due to penetration of compressor room's duct, lift m/c room at stair-2 and the security server room at stair-1. On 07-Jan-26: The factory has installed a fire-rated door at the ground floor of Stair-01 to separate the security server room, removed a duct from the compressor room at the ground floor of Stair-02, and sealed the unprotected opening from the lift machine room at Stair-02. However, several ducts (BBT into ducts) are still located within Exit Stair-02 at the ground floor. Additionally, Exit Stair-01 is still not properly separated from the lift machine room due to unprotected openings at the roof floor of Stair-01. Furthermore, unprotected openings within Stair-01 on the 1st floor which are exposed to other parts of the building at an angle of less than 180 degrees (3.14 rad). | Within 3 months | In Progress
Initial Inspection |  | 2 | Areas used for combustible storage at several floors open to the factory are not separated by fire rated construction. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m.or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction | Factory has removed all storage area from production floor. | Jun 1 2023 | On 20/09/2023: Corrected as per site condition. No heavy load was observed during the inspection. On 07-Jan-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Unsealed floor penetrations through Toilets, Sanitary Pipe, Fire cables shaft (inside), Floor windows (direct west side) are located in the fire-rated floor/ceiling assemblies. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's datasheet Or Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | The facility management has sealed sanitary pipe by brick wall , protected window and fire alarm cable shaft sealed. Work Done | Jun 1 2023 | On 20/09/2023: Work in progress. Sanitary pipe has been sealed by brick wall, but unprotected window and fire alarm cable shaft were found unsealed. On 07-Jan-26: The factory has sealed the cable duct partially using concrete mortar; however, the sealing did not cover the full slab thickness. The window openings remain the same as before including exterior facade wall. Furthermore, several plastic plumbing pipe penetrations were found unsealed, while some were sealed using pipe collars. The factory is recommended to submit credible supporting documents for the installed pipe collars to the RSC for review and ensure installation in accordance with the listed design guidelines. As an alternative, concrete mortar may be used to seal cable penetrations if the opening area is less than 144 sq. in. | Within 3 months | In Progress
Initial Inspection |  | 4 | Elevator shafts are directly open into the inside of exit stair enclosure. Location: Stair 1 (South-West) and Stair 2 (South-East) of production building. | Modify the elevator shaft as per RSC Technical Guideline (Standard) V1-6.14.3. An exit stairway shall not be built around a lift shaft unless both of them are located in a smoke proof enclosure and made of a material with fire resistance rating required for the type of construction of smoke proof enclosure. So, ensure the lift shaft is 2-hr fire rated including opening protection with similar rating. | Facility has listing tag at lift landing door. And available as required documents (Datasheet & Design drawing with Certificate). Done | Jun 1 2023 | On 20/09/2023: During the inspection no listing tag was found at the lift landing door. The factory has provided the documents of lift landing door which was incomplete. Factory shall provide the datasheet, certificate & design drawing of lift landing door. On 07-Jan-26: The factory has informed that the installed lift landing doors are fire rated and provided a Type Examination Certificate for review. However, only Type Examination Certificate is not sufficient for verification. A Type Examination Certificate only confirms that a sample (type) of the product was tested by a notified body; it does not confirm that the specific product being supplied to the project is compliant with the approved type, and it does not demonstrate that the certification body has conducted regular surveillance of the product. The factory shall provide the Product Certificate or Certificate of Conformity (CoC) issued by the certification body, along with the lift landing door datasheet, serial number, and test report for the installed lift landing door. | Within 3 months | In Progress
Initial Inspection |  | 5 | Bonded ware house at stair 2 (1st floor), FG warehouse at stair 1 (1st floor) and accessories store at stair 2 (5th floor) discharge directly into the exit stair enclosures and are not meet the RSC Technical Guidelines (Standard) V1- 6.14.3) | Openings from exit enclosure to storage rooms shall be provided with a vestibule with fire rated construction and openings as per RSC Technical Guideline (Standard) V1-6.14.3. Provide a 1.5 hr. fire rated door on the exit stair side and a 1-hr. fire rated door on the Store room side. Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure. | Factory has updated architectural floor layout (which is attached with all documents) in which store locations has been changed and are not directly opened to any exit stair. | Jun 1 2023 | On 20/09/2023: Corrected. During the inspection no accessories store was found at 5th floor dining area and the 1st floor store was found vacant. Reportedly the factory informed that the 1st floor will be used as sewing section. On 07-Jan-26: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Dining room and Prayer room are located at 1st floor are not properly fire separated from other occupancy by fire rated construction. | Separate the dining & prayer room from production & other occupancies (present sample section) by minimum 3-hr fire rated construction. Provide rated exit passageways leading directly to the exit stairs with the same resistance rating. | Facility has provided separate fire rated door for exit stair. Done | Jun 1 2023 | On 20/09/2023: During the inspection the dining room was found at 5th floor which was not separated properly. Factory shall provide the rated exit passageways leading directly to the exit stairs with the same resistance rating. On 07-Jan-26: The factory is separating the dining area from the office area using fire-rated construction; however, the work has not yet been completed due to remaining several unsealed penetrations and openings, non-rated door etc. | Within 3 months | In Progress
Initial Inspection |  | 7 | A single means of egress is provided at Finished goods warehouse located at 1st floor, where the travel distance exceeds 75 feet (or, 23 meter) and does not meet the RSC Technical Guidelines (Standard) V1- 6.6.2) | Reconfigure the egress arrangement to reduce the maximum travel distance to not more than 23 meter (or, 75 feet).Or, -Provide additional means of egress. | Facility has provided secondary means of Egress. Done | Jun 1 2023 | On 20/09/2023: During the inspection still a single means of egress was found at 1st floor which was vacant. Reportedly the factory informed that the 1st floor will be used as sewing section. However; Factory shall rearrange the egress to reduce the maximum travel distance not more than 75ft or provide additional means of egress. On 07-Jan-26: Corrected. The factory has demolished the separation wall and is currently using the 1st floor as a sewing section. A total of three exits are available on this floor, and the required number of exits are meet. | Within 3 months | Corrected
Initial Inspection |  | 8 | Compressor room located at ground floor is not properly separated by fire rated construction with exit stair enclosure 2. | Separate the compressor room by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain fire separations. Or, Relocate all to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | This same finding is pointed at inspection observation no 01. So requesting to close inspection observation no.08 The facility management has done the compressor room separated properly. Work Done | Apr 1 2023 | On 20/09/2023: The compressor room was not separated properly due to duct opening. On 07-Jan-26: The factory has removed a duct from the compressor room at the ground floor of Stair-02; however, several ducts (BBT into ducts) are still located within Exit Stair-02 at the ground floor from the compressor room. | Within 1 month | In Progress
Initial Inspection |  | 9 | Fire alarm and detection system installation requires detailed review to confirm compliance with NFPA 72 and RSC Technical Guidelines (Standard) V1. | Submit design, documents and calculations to RSC for review prior and based on the review modify the system if there is any. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the fire detection & alarm system installation. Also inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | The facility management submitted as build drawing (FADS) according to NFPA and Reviewed by RSC. Factory has completed installation as per reviewed drawing. Also we have submitted all related revised documents as per comments of Pre T&C date on 16.03.2025. Work Done | Sep 1 2023 | On 20/09/2023: Work in progress. The factory has resubmitted the design & drawing of Fire Alarm & Detection System to RSC on dated 07/09/2023 for review. The review process is ongoing. On 17-Jun-2025: Pre-T&CVI was conducted, and it was found that desktop document verification is required. Please see the details in the Pre-T&CVI report. On 07-Jan-26: T&CVI for FADS has been conducted along with the FUI and found that the system is approved. Please see the details in the T&CVI report. | Design Review within 2 months and modification within 4 months (If require). | Corrected
Initial Inspection |  | 10 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72 | The facility management submitted as build drawing (FADS) according to NFPA and Reviewed by RSC. Done | Oct 1 2023 | On 20/09/2023: It is an integrated part of Fire Alarm & Detection System. On 17-Jun-2025: Corrected. The factory has maintained Fire Alarm & Detection System as per requirements. Documents were available on-site. On 07-Jan-26: Corrected. | Within 1 month (after installation) | Corrected
Initial Inspection |  | 11 | Standpipe system and fire pump installation requires detailed review to confirm compliance with NFPA 14 ,20 ,22, 24 and 25 and as per RSC Technical Guidelines (Standard) V1. | Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with Accord standard and NFPA 14 and 20. The factory management shall contact RSC to conduct the final acceptance testing after the installation, testing & commissioning. | The facility management submitted as build drawing (SUPS) according to NFPA. Already Reviewed by RSC. Factory has completed installation as per reviewed drawing. Also we have submitted all related revised documents as per comments of Pre T&C date on 16.03.2025. Work Done | Sep 1 2023 | On 20/09/2023: Work in progress. The factory has resubmitted the design & drawing of Fire Protection System to RSC on dated 07/09/2023 for review. The review process is ongoing. On 07-Jan-26: Pre-T&CVI for SUPS has been conducted along with the FUI and found that the system is not ready for full functional T&CVI. Initial design review is required due to major remediation work. Please see the details in the Pre-T&CVI report. | Design Review within 2 months and modification within 4 months (If require). | In Progress
Initial Inspection |  | 12 | Inspection, testing, and maintenance for the Standpipe system is not in accordance with NFPA 25 or as per RSC standard. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 or as per RSC standard. | Facility has maintained Inspect, test and maintain the standpipe system and kept written records on-site, in accordance with NFPA 25 or as per RSC standard. and submitted Pre T&C related all SUPS documents and reviewed by RSC. Work Done | Oct 1 2023 | On 20/09/2023: It is an integrated part of Fire Protection System. On 07-Jan-26: It is an integrated part of Fire Suppression System. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 13 | Inspection, testing, and maintenance for the Fire pump & water system is not in accordance with NFPA 25 or as per RSC standard. | Inspect, test and maintain the fire pump & water system and keep written records on-site, in accordance with NFPA 25 or as per RSC standard. | Facility has maintained Inspect, test and maintain the fire pump & water system and kept written records on-site, in accordance with NFPA 25 or as per RSC standard. and submitted Pre T&C related all SUPS documents and reviewed by RSC. Work Done | Oct 1 2023 | On 20/09/2023: It is an integrated part of Fire Protection System. On 07-Jan-26: It is an integrated part of Fire Suppression System. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 14 | Building did not have stair designation signs at floor entrances and re-entry provisions where every door in a stair enclosure serving more than 5 stories. | Provide stair designation signs at required locations and every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets the requirements of RSC Technical Guidelines (Standard) V1- 6.8.3.1. | Factory has provided stair designation signs at required locations and every door in a stair. | Apr 1 2023 | On 20/09/2023: Corrected. Stair designation sign and re-entry were posted at required location. On 07-Jan-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 15 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Factory has tested the emergency lighting system on each floor and provided adequate emergency fixtures to provide adequate illumination along the means of egress. | Apr 1 2023 | On 20/09/2023: Corrected. Found okay. On 07-Jan-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 16 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with NFPA 10. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with NFPA 10. Keep written records on-site. | Factory has inspected, tested and maintaining the exit sign and emergency lighting system in the accordance with NFPA 10 and keeping written records on-site. | Apr 1 2023 | On 20/09/2023: Corrected. On 07-Jan-26: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 17 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on-site, in accordance with NFPA 10. | Factory has inspected, tested and maintaining the portable fire extinguishers and keeping written records on-site, in accordance with NFPA 10. | Apr 1 2023 | On 20/09/2023: Corrected. On 07-Jan-26: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding (2nd FUI): Doors in a means of egress was found less than 1 m (39 inch) (found 30 inch). Location: 5th floor near stair-03 & ground floor inspection office area (Newly installed). | Doors in a means of egress shall have a minimum width of 1 m (39 in.) as per RSC Technical Guideline (Standard) section of 6.5.6 | In Progress | Apr 7 2026 | On 07-Jan-26: New Finding. | Within 3 months | In Progress
Follow Up Inspection |  | 19 | New Finding (2nd FUI): Unsealed penetrations and openings including server box were located in exit stair enclosures. Electrical cable & BBT raceway (BBT into ducts) passing through the exit enclosure. Location: Stair-02 & 03; most of the floors. | No other penetration into and through the exit enclosure except for fire alarm equipment electrical raceway, required exit doors, sprinkler piping, standpipes, and electrical conduit serving the exit enclosure is permitted in accordance with section 6.14.4 of RSC Technical Guidelines (Standard)¹ V1.0. So, relocate the electrical wires/raceways to somewhere else avoiding the exit enclosure, and seal the created unprotected openings with a minimum of 1.5 hours listed/certified fire-rated materials. Installation shall be as per manufacturer published installation guideline and the certification authority guideline to ensure the fire-rating. Or seal the penetration by 2-hr masonry construction. | In Progress | Apr 7 2026 | On 07-Jan-26: New Finding. | Within 3 months | In Progress
Follow Up Inspection |  | 20 | New Finding (2nd FUI): Storage areas discharges directly into the exit stair enclosure. Location: Stair-02; Ground floor (Newly occupied as storage). | Openings from exit enclosure to storage areas shall be provided with a vestibule with fire rated construction and openings in accordance with section 6.14.3 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a min 1-hr fire rated door on the exit stair side and a 1.5 hr. fire rated door on the store side . Ensure that the fire rating of the vestibule construction matches that of the exit stair enclosure as per RSC Technical Guidelines (Standard)¹ V1.0. section 6.14.3. The minimum width for vestibules shall not be less than 1.1m and length 1.8m. | In Progress | Apr 7 2026 | On 07-Jan-26: New Finding. | Within 3 months | In Progress

## Electrical
Date
04-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Ingenitex (BD) Limited, Jamgora , Ashulia, Dhaka, Dhaka, Dhaka
Date of Inspection |  | 2023-02-13
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | SLD has been Accepted by RSC. | Jun 1 2023 | On 20/09/2023: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 2 | Inadequate working space around transformer for performing maintenance work. No working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear). | A working separation between LT and HT must be ensured. A brick wall will do it. Adequate working clearance (1.07m) and ventilation must be ensured. | A brick wall separation between LT & HT has been made ensuring adequate working clearance (1.07m) and ventilation also ensured. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 3 | Transformer Breather oil cup is not filled properly. | Transformer breather oil cup must be filled up to the oil mark on the cup. | Oil cup has been filled up to the oil mark on the cup | Apr 1 2023 | On 20/09/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 4 | Equipment earth cable (for generator) is not available. | Provide earthing connection for generator. At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | Factory has provided four earth pit for each generator (two for body grounding, two for neutral). All earthing connection has been made as per BNBC standard. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 5 | Heat shields/blankets missing to protect component and operator from excessive heat. | Heat shields/blankets must be installed to shield hot surface to protect component and operator from excessive heat. Proper guards shall be provided after shielding hot surface. Blankets on exhaust manifold, turbocharger housing and other engine components is not necessary. Suggested to consult with the generator supplier/service provider/expert before doing the job. | Heat shields has been installed to shield hot surface to protect component and operator from excessive heat. Proper guards has been provided after shielding hot surface. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 6 | HT panel board are inaccessible or cannot be opened to perform any maintenance work. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degrees. | Factory has provided a stair as per standard to access the HT panel easily and make enough space to perform maintenance work | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 7 | Improper terminations are available at panel boards. | Cables needs to be terminated in busbar with proper sized cable lugs, washer, nut-bolts with direct contact to the buses. No busbar tubes shall be in between the contacts. | Cables has been terminated in busbar with proper sized cable lugs, washer, nut-bolts with direct contact to the buses. busbar tubes has been removed in between the contacts. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 8 | Panel body is not connected to earth. Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Panel body has been connected to earth. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 9 | MCCBs/MCBs are not installed/adjusted per load demand. | All the MCCBs/MCBs must be installed/adjusted as per connected load current; if adjustment is not possible, replacement will be the only way. | MCCBs/MCBs are now installed and adjusted per load demand. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 10 | Hot spots have been observed at some points (Above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Hot spots has been eliminated from entire electrical system. | Mar 15 2023 | On 20/09/2023: Corrected. | 2 WEEKS | Corrected
Initial Inspection |  | 11 | BBT plug point left open. | Unused BBT plug point must be sealed/covered by BBT plug cap or by insulating material. | Unused BBT plug point has been covered by BBT plug cap. | May 1 2023 | On 20/09/2023: Corrected. | 2 MONTHS | Corrected