## Structural
Date
06-Jul-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Lakhsma Innerwear Ltd, South vangnahati, Sreepur, Gazipur, Gazipur
Date of Inspection |  | 2018-11-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Future extension to be carried out. | Additional soil test are required to justify the bearing capacityof soil for the existing structure. | Done | Jan 13 2019 | On 17-July-2019: During inspection additional soil test report was not found. Factory management is required to prepare a soil test report as per initial report recommendation. On 10-Dec-2020: As a part of DEA factory management have prepared additional soil test report dated on August-September, 2019. Factory management have submitted revised DEA (Proposed 5-storied) including additional soil test report to RSC over mail on 10-December-2020 which is under review. On 26-Oct-2021: During inspection, A set of soil test report dated on August-September, 2019 was found on site which was incorporated in DEA. DEA documents for the extension of proposed five-storied Main Factory Building of the factory was accepted by RSC on 23-Jan-2021. On 19-Nov-2024: Corrected previously. | 6 weeks | Corrected
Initial Inspection |  | 2 | Future extension to be carried out. | Based on the additional geotechnical investigation report | Done | Jan 13 2019 | On 17-July-2019: This issue is required to be covered in DEA report but submission of DEA report is pending. During inspection additional soil test report was not found. Factory management is required to prepare a soil test report as per initial report recommendation. On 10-Dec-2020: As a part of DEA factory management have prepared additional soil test report dated on August-September, 2019. Factory management have submitted revised DEA (Proposed 5-storied) including additional soil test report to RSC over mail on 10-December-2020 which is under review. On 26-Oct-2021: During inspection, A set of soil test report dated on August-September, 2019 was found on site which was incorporated in DEA. DEA documents for the extension of proposed five-storied Main Factory Building of the factory was accepted by RSC on 23-Jan-2021. On 19-Nov-2024: Corrected previously. | 6 weeks | Corrected
Initial Inspection |  | 3 | Future extension to be carried out. | For vertical extension, complete Detail Engineering Assessment (DEA) addressing the observations. | Done | Feb 6 2019 | On 17-July-2019: Factory management has an intension for vertical extension but still construction work not started. So, this issue is required to be covered in DEA report but submission of DEA report is pending. During inspection additional soil test report and core test report were not found. Factory management is required to prepare a DEA report as per initial report recommendation. On 10-Dec-2020: This issue had been covered in DEA report. Factory management have submitted revised DEA report (Proposed 5-storied) to RSC over mail on 10-December-2020 which is under review. On 26-Oct-2021: Factory has carried out DEA for the extension of proposed five-storied Main Factory Building. DEA of the factory was accepted by RSC on 23-Jan-2021. During inspection, building extension work was found completed. No discrepancy was observed at the Main Factory Building as well as no retrofitting work is required as per DEA recommendation. On 19-Nov-2024: Corrected previously. During inspection the Factory Building was found as 5 storied as per accepted drawing. However, during inspection undesignated storage was found on 4th floor and office was found instead of production area on 1st floor. Change was check and analysis result was found satisfactory. Update as-built drawing and keep on site. | 6 month | Corrected
Initial Inspection |  | 4 | Future extension to be carried out. | Vertical extension to be carried out as per recommendation of DEA. | DEA is approved and vertical extension already 95% done and need to15 days for fire and electric work. Fire and electric work done 25% | Feb 6 2019 | On 17-July-2019: Factory management has an intension for vertical extension but still construction work not started. So, this issue is required to be covered in DEA report but submission of DEA report is pending. During inspection additional soil test report and core test report were not found. Factory management is required to prepare a DEA report as per initial report recommendation. On 10-Dec-2020: This issue had been covered in DEA report. Factory management have submitted revised DEA report (Proposed 5-storied) to RSC over mail on 10-December-2020 which is under review. After receiving DEA acceptance future extension will be carried out as per recommendation. On 26-Oct-2021: Factory has carried out DEA for the extension of proposed five-storied Main Factory Building. DEA of the factory was accepted by RSC on 23-Jan-2021. During inspection, building extension work was found completed. No discrepancy was observed at the Main Factory Building as well as no retrofitting work is required as per DEA recommendation. On 19-Nov-2024: Corrected previously. | 6 month | Corrected
Initial Inspection |  | 5 | Exposed rebar at roof. | Apply rust proof coating to the exposed rebar. | Corrected | Jan 13 2019 | On 17-July-2019: Factory management has applied rust proof coating to the exposed rebar. On 10-Dec-2020: Corrected from previous follow up inspection of Accord. During inspection rust proof coating was found on exposed rebar. On 26-Oct-2021: Corrected previously. No exposed rebar at the roof of main factory building was found during inspection. On 19-Nov-2024: Corrected previously. No exposed rebar was found. | 6 weeks | Corrected
Initial Inspection |  | 6 | Missing bracing at end frame. | Installed missing bracing as per specification. | Corrected | Jan 13 2019 | On 17-July-2019: Factory management has installed missing bracing at end frame. On 10-Dec-2020: Corrected from previous follow up inspection of Accord. Missing bracing at end frame was found installed. On 26-Oct-2021: Corrected previously. No missing bracing was found at end frame of the sewing shed. On 19-Nov-2024: Corrected previously. No missing bracing was found. | 6 weeks | Corrected
Initial Inspection |  | 7 | Corrosion on steel member. | Apply rust proof coating on steel member | Done | Jan 13 2019 | On 17-July-2019: Factory management has applied rust proof coating on steel member. On 10-Dec-2020: Corrected from previous follow up inspection of Accord. During inspection rust proof coating was found on steel member. On 26-Oct-2021: Corrected previously. Factory management has painted the corroded steel members of sewing shed. On 19-Nov-2024: Corrected previously. Factory provided rust proof paint on steel members. | 6 weeks | Corrected
Follow Up Inspection |  | 8 | New finding-1: Undocumented structure found in factory premises (Dining Shed -single storied bamboo-wooden structure -2600 sft). Minor sagging and poor connection were observed on the wooden rafter. | Replace the Shed with a well designed structure. | In process | Dec 31 2024 | RPO Comments: On 14/12/2025 - No timeline extension is accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 19-Nov-2024: During inspection, an undocumented structure was found in the factory premises (Dining Shed -single-storied bamboo-wooden structure -2600 sft). Minor sagging and poor connection were observed on the wooden rafter. The factory is required to replace the shed with a well-designed structure. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 9 | New finding-2: Undocumented structure found in factory premises (Prayer Shed-Single storied-480 sft, Security & Fire Control Room-Single storied RC -350 sft, Boiler Room-Single storied shed-400 sft.). Lack of as-built drawing. | Produce as-built drawing and keep on site. | Corrected | Dec 31 2024 | RPO Comments: On 14/12/2025 - The factory management reported the remediation completion. This item will be verified in the next inspection On 19-Nov-2024: During inspection, undocumented structures were found in factory premises (Prayer Shed-Single storied-480 sft, Security & Fire Control Room-Single storied RC -350 sft, Boiler Room-Single storied shed-400 sft.). The as-built drawing was not found on site. The building engineer is required to produce as-built drawings and keep on site. | (within 6 weeks) | Pending Verification

## Fire
Date
06-Jul-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Lakhsma Innerwear Ltd, South vangnahati, Sreepur, Gazipur, Gazipur
Date of Inspection |  | 2018-11-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Areas used for in-process storage of combustible materials are open to the surrounding occupancy. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m.2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m.or3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Corrected | Mar 2 2019 | On 11-9-2019: Not corrected yet. On 01-01-2023: Observed huge in process storage at 1st, 2nd and 3rd floor. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 2 | Boiler units are located inside the staircase enclosure without any fire separation. | Provide minimum 1-hr fire rated construction to separate the boiler room from other occupancies. | Boiler units are sifted in different building | Mar 2 2019 | On 11-9-2019: Not completed yet. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 3 | Dining area are not separated by proper fire rated construction. Location: 2nd floor. | Separate the dining rooms by minimum 1-hr fire rated construction from any other occupancy. The opening protective shall also be minimum 1-hr fire rated. Also ensure direct access to exit stair from dining. | Dinning & canteen room are sifted in different shed | Mar 2 2019 | On 11-9-2019: Not corrected yet. On 01-01-2023: Corrected. Dining area is not at 2nd floor anymore. It is relocated to a safe location. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 4 | Aisles were found obstructed by process goods/sewing tables/finished cartons at several locations throughout the factory. | Aisles shall always be free of any kind of obstruction. Provide minimum clear aisle widths of 36-inch. | Corrected | Dec 9 2018 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 5 | Building did not have stair designation signs and occupant load signs at the required locations. | Provide stair designation signs and occupant load signs at a conspicuous space near floor entries. | Corrected | Jan 2 2019 | On 11-9-2019: Not corrected. On 01-01-2023: Not corrected yet. Not provided at few floors at the required locations. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 1 month | Corrected
Initial Inspection |  | 6 | Egress doors/gates with locking features not complying with NFPA101 are provided at building exits at ground & 1st floor. | Remove locking features from all egress doors/gates.If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | Corrected | Dec 9 2018 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Penetrations through fire rated floor/staircase assemblies were found unsealed. | Seal all penetrations and openings in floor/staircase (full/required thickness ) assemblies by listed fire rated materials to maintain the required fire resistance rating. | Corrected | Mar 2 2019 | On 11-9-2019: Fire doors need to be interfaced with FA system. Maintenance required. On 01-01-2023: Observed few penetrations and accessories of fire doors need to be maintained also. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 8 | Penetrations / Openings through fire rated floor/ceiling assemblies were found unsealed. | Seal all penetrations and openings in floor/ceiling (full/required thickness ) assemblies by listed fire rated materials to maintain the required fire resistance rating. | already 50 % work completed and others materials have been estimates, work will starts soon. | Mar 2 2019 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 9 | The factory building has an occupied floor (as per architectural drawing) greater than 10 meter (33 feet). | Design & install a new class III standpipe system & fire department (Siamese) connection in accordance with NFPA 14. The standpipe system shall be connected to a dedicated fire pump meeting minimum hydraulic demands of NFPA 14 & Accord standard at the required points. Installation of the fire pump shall be as per NFPA 20. Submit the design to Accord for review and approval before installation.Upon approval & installation the owner shall contact the Accord prior to conducting the final acceptance testing of the standpipe system installation.Also inspect, test and maintain the standpipe system & fire pumps, and keep written records on-site, in accordance with NFPA 14, 20 and ACCORD standards. | Corrected | Sep 2 2019 | RPO Comments: On 03/03/2026 - The design documents (FADS-SUPS) are currently under RSC’s review. On 11-9-2019: Design has been submitted for review. On 01-01-2023: Modification work is still ongoing. Factory shall submit documents to RSC for T&C as soon as possible after the completion of modification work. On 8/1/2023: Installation work almost done. On 01-Sep-2024: Pre-T&CVI was conducted & it was found that the factory is not ready for full functional T&CVI. Please see the details in the Pre-T&CVI report. On 10-Dec-25: After the Pre T&C on 01 Sep, 2024 a meeting was conducted on 21 April 2025. According to the meeting conducted on 21 April 2025, the factory was required to submit the proposed fire protection system drawing to the RSC for review. The factory submitted the updated proposed drawing softcopy to the RSC on 20 Oct, 2025. The submitted documentation did not include several documents and also required to be updated the proposed drawing. The factory is required to submit the revised and additional documents to the RSC for proposed drawing review. | Design within 3 months; Install within 6 months. | In Progress
Initial Inspection |  | 10 | The factory has been installed sprinkler system in factory building, But not installed as per standard. | Factory need to maintain the sprinkler system as per standard/ NFPA-13. | Corrected | Sep 2 2019 | RPO Comments: On 03/03/2026 - The design documents (FADS-SUPS) are currently under RSC’s review. On 11-9-2019: Design has been submitted for review. On 01-01-2023: Modification work is still ongoing. Factory shall submit documents to RSC for T&C as soon as possible after the completion of modification work. On 8/1/2023: Rack sprinkler is missing in the storage area. On 01-Sep-2024: Pre-T&CVI was conducted & it was found that the factory is not ready for full functional T&CVI. Please see the details in the Pre-T&CVI report. On 10-Dec-25: After the Pre T&C on 01 Sep, 2024 a meeting was conducted on 21 April 2025. According to the meeting conducted on 21 April 2025, the factory was required to submit the proposed fire protection system drawing to the RSC for review. The factory submitted the updated proposed drawing softcopy to the RSC on 20 Oct, 2025. The submitted documentation did not include several documents and also required to be updated the proposed drawing. The factory is required to submit the revised and additional documents to the RSC for proposed drawing review. | Design within 3 months; Install within 6 months. | In Progress
Initial Inspection |  | 11 | Fire pumps are provided and needed to meet as per Accord Building Standard 5.5.1 | Provide fire pumps.Installation of the fire pumps shall be required to provide shop drawing & hydraulic calculations as outlined in NFPA 13, 20, 22 and 24. These drawings shall include all details as outlined in NFPA 13, 20, 22 & 24.All fire protection water supply system installation design documents shall be submitted for review by the Chief Safety Inspector of Accord prior to commencement of installation.Upon approval & installation the owner shall contact the Accord prior to conducting the final acceptance testing of the installation to allow the Accord the option of witnessing this esting & conduct a final inspection of the installation. | corrected | Sep 2 2019 | RPO Comments: On 03/03/2026 - The design documents (FADS-SUPS) are currently under RSC’s review. On 11-9-2019: Design has been submitted for review. On 01-01-2023: Modification work is still ongoing. Factory shall submit documents to RSC for T&C as soon as possible after the completion of modification work. On 8/1/2023: Sprinkler is required inside the pump room area. On 01-Sep-2024: Pre-T&CVI was conducted & it was found that the factory is not ready for full functional T&CVI. Please see the details in the Pre-T&CVI report. On 10-Dec-25: After the Pre T&C on 01 Sep, 2024 a meeting was conducted on 21 April 2025. According to the meeting conducted on 21 April 2025, the factory was required to submit the proposed fire protection system drawing to the RSC for review. The factory submitted the updated proposed drawing softcopy to the RSC on 20 Oct, 2025. The submitted documentation did not include several documents and also required to be updated the proposed drawing. The factory is required to submit the revised and additional documents to the RSC for proposed drawing review. | Design within 3 months; Install within 6 months. | In Progress
Initial Inspection |  | 12 | The Compressor room is not separated by fire rated construction with pump room. (openings/penetrations/non rated ceilings). | Separate the Compressor room by a minimum 2-hr fire rated construction along with a Type-I (BNBC 2006) ceiling construction. Seal and/or protect all openings to maintain fire separations with pump room. | Corrected | Mar 2 2019 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 13 | Several exits are not provided with exit signage's. Directional exit signs were missing at the change of exit direction. | Provide illuminated exit signs at every floor and room exits. Provide illuminated directional exit signs where the change of direction is not obvious. | Done | Jan 2 2019 | On 11-9-2019: Not corrected. An exit sign at ground floor was not working. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 01 month | Corrected
Initial Inspection |  | 14 | Storage was located under the cutting table. | Remove all storage from under the cutting table.. | Corrected | Dec 9 2019 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 15 | Egress doors/gates with locking features/slide bolts not complying with NFPA101 are provided at exits. | Remove locking features/slide bolts from all egress doors/gates.If locks are required for security reasons, utilize specialized door locking features complying with NFPA101. | Corrected | Dec 9 2019 | On 11-9-2019: Corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 16 | Room used for combustible storage is open to the dining area and not separated by proper fire rated construction. | Separate the storage room by minimum 1-hr fire rated construction from any other occupancy. The opening protective shall also be minimum 1-hr fire rated. | Corrected | Mar 2 2019 | RPO Comments: On 03/03/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11-9-2019: Not completed yet. On 01-01-2023: Fire doors were kept opened with unauthorized external sources. On 8/1/2023: Still fire door is missing in the bonded warehouse area. On 10-Dec-25: Fire rated doors have been installed and unprotected opening has been sealed by the fire rated construction. Additionally, gypsum board has been used for the separation work. Design no. U412 has been submitted as the reference of the installation of gypsum board. But the gypsum board did not have label on it. Batt and blanket datasheet and certification have not been found during the inspection. | 03 month | Pending Verification
Initial Inspection |  | 17 | The fire detection system has been provided by the factory but drawing is not reviewed by the Accord & Installation shall be verified by the Accord. | Design and install an addressable fire detection & alarm (Audio & Visual) system replacing the existing one in compliance with NFPA 72 & Accord standard. Submit the design to Accord for review and approval before installation.Upon approval & installation the owner shall contact the Accord prior to conducting the final acceptance testing of the fire detection & alarm system installation. | Corrected | Jan 2 2020 | RPO Comments: On 03/03/2026 - The design documents (FADS-SUPS) are currently under RSC’s review. On 11-9-2019: Design has been submitted for review. On 01-01-2023: Modification work is still ongoing. Factory shall submit documents to RSC for T&C as soon as possible after the completion of modification work. On 8/1/2023: Installation work almost done. On 01-Sep-2024: Pre-T&CVI was conducted & it was found that the factory is not ready for full functional T&CVI. Please see the details in the Pre-T&CVI report. On 10-Dec-25: After the Pre T&C on 01 Sep, 2024 a meeting was conducted on 21 April 2025. According to the meeting conducted on 21 April 2025, the factory was required to submit the proposed fire protection system drawing to the RSC for review. The factory submitted the updated proposed drawing softcopy to the RSC on 6 Nov, 2025. The submitted documentation did not include several documents and also required to be updated the proposed drawing. The factory is required to submit the revised and additional documents to the RSC for proposed drawing review. Fire alarm control panel has been found in shutoff condition. The factory reported that the fire alarm control panel is faulty and requires troubleshoot of the circuit board. The factory should ensure that the fire alarm control panel is functional with high priority. The factory did not share any tentative date for the submission of the fire detection system proposed drawing to the RSC during the inspection. | Design within 4 months; Installation within 9 months | In Progress
Initial Inspection |  | 18 | Inspection, testing, and maintenance for the fire detection & alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire detection & alarm system, and keep written records on-site, in accordance with NFPA 72 | Corrected | Mar 2 2019 | RPO Comments: On 03/03/2026 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 11-9-2019: Not corrected. Panel was not free from faults. On 01-01-2023: It is an integrated part of FADS. Panel was not free of faults. On 8/1/2023: It is an integrated part of FADS. On 01-Sep-2024: Pre-T&CVI was conducted & it was found that the factory is not ready for full functional T&CVI. Please see the details in the Pre-T&CVI report. On 10-Dec-25: It is an integrated part of FADS. | 03 month | Pending Verification
Initial Inspection |  | 19 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Corrected | Mar 2 2019 | On 11-9-2019: Not as per NFPA 10. On 01-01-2023: Not maintaining as per NFPA 10. On 8/1/2023: No documents has been found. On 10-Dec-25: Corrected. Written record of inspection, testing and maintenance has been provided for the fire extinguisher during the inspection. | 03 month | Corrected
Initial Inspection |  | 20 | Building did not have occupant load signs at required locations. | Provide occupant load signs at required locations. | Corrected | Dec 9 2019 | On 11-9-2019: Not provided. On 01-01-2023: Not provided at all floors. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 01 month | Corrected
Initial Inspection |  | 21 | Manual on-off switch is provided for emergency lighting units. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | Jan 2 2019 | On 11-9-2019: Not corrected. On 01-01-2023: Observed at ground floor only. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 01 months | Corrected
Initial Inspection |  | 22 | The exit discharge path is less than 10 ft. wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. | Done | Mar 2 2019 | On 11-9-2019: Not corrected. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Initial Inspection |  | 23 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Done | Mar 2 2019 | On 11-9-2019: Inadequate. On 01-01-2023: Corrected. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 03 month | Corrected
Follow Up Inspection |  | 24 | New Finding (2nd FUI): IPS and Battery have been observed under Stair 1. | Remove/relocate IPS/Battery from under the stair and keep it clear. | Corrected | Feb 1 2023 | On 01-01-2023: New finding. On 8/1/2023: Corrected. On 10-Dec-25: Corrected. | 01 month | Corrected
Follow Up Inspection |  | 25 | New Finding (2nd FUI): Unsealed openings were located at 1st floor fire-rated floor from sewing section at ground floor. | Seal/Protect all openings in floor by fire rated material to maintain the fire separation. | Corrected | Feb 1 2023 | RPO Comments: On 03/03/2026 - The factory management reported the remediation completion but no evidence has been shared. On 01-01-2023: New finding. On 8/1/2023: Issue has been found same as before. On 10-Dec-25: Found same as the previous condition. | 01 month | In Progress
Follow Up Inspection |  | 26 | New Finding (2nd FUI): The main structural elements of the sewing shed building (Newly constructed shed) are constructed by steel which is non-rated and were found in exposed condition without any fire protection. | The building shall be type-I or II construction. So, provide require rating in the structural elements of the building. Consult with a qualified fire protection engineer. Follow BNBC 2006-Table 3.3.1, 3.2.4 & 3.1.9. | In Progress | Jul 1 2023 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 01-01-2023: New finding. On 8/1/2023: No action has been taken yet. On 10-Dec-25: As per RSC Technical Guideline and BNBC 2006, The Fire rating of the structure requires to be confirmed as per BNBC 2006. The "Ministry of Housing and Public Works” has issued a resolution based on the recommendations from the House Building Research Institute (HBRI) and the Public Works Department (PWD) to assess structural fire protection requirements of steel buildings (unprotected non-combustible construction type) according to BNBC 2020. The construction type shall confirm to be in accordance with BNBC 2020 Part-3, Table 3.1.7. Ensure fire resistive rated construction following Table 3.3.1 (a) Part 3 Section-3, Table 3.2.2 and Table 3.2.3 Part 3 Section 2 and Table 4.1.1 from BNBC 2020 Part 4 Section 1. However, based on the on-site assessment following BNBC 2020, building height of thebuilding has been found as followes. Shed Building 1: The shed is in single fire compartment with the 5 storied Factory Building. Peak height and eve height of the shed is 24'1" and 18'4" respectively, Plinth height 3'6". Average height is 7.53 meter (24.7 feet). Main building height is 55 feet (Upto unoccupied roof level) and 45 feet (Highest occupied floor). North: Main building at 0" apart, South: Boundary wall at minimum 6' to maximum 17'6" apart, West: Boundary and open yard at 6'6" apart, East: Shipping container at 49'10". Submit the design philosophy for the Shed building 1 for the structural fire resistance rating or provide required fire rated separation between the Shed 1 and the Factory Building according to the mentioned standard. Single Storied Godown: Building height has been found peak height and eve height 14'1" and 12'4" respectively. Average height is 4.02 meter (13.2 feet). North: Utility building at 12' apart, South: Temporary dining at 15 feet apart, East: Boundary wall at minimum 0' to maximum 46' apart, West: Container at 16'2" apart Medical and Child Care Shed Building: Building height has been found peak height and eve height 11'1" and 10' respectively. Average height is 3.02 meter (10.05'). North: Utility building at 120' apart, South: Temporary prayer shed at 8 feet apart, East: Single storied godown at 58' apart, West: Shed building 17.20 feet apart As per section 3.1.7 of BNBC 2020, the building type of the Single Storied Godown and Medical and Child Care Shed Building have been determined as type - I-E. Hence, Structural Fire Protection of the main structural elements are not required but exterior wall rating is rquired to be ensured as per Table 3.2.2, Table 3.2.3 and Table 3.3,1 (a). | 06 months | In Progress
Follow Up Inspection |  | 27 | New Finding (4th FUI): Directional signs are not provided where direction of the path of travel to an exit has changed. Location: Factory building and shed 1. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | In Progress | Jan 10 2026 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 10-Dec-25: New Finding. | Within 1 Month | In Progress
Follow Up Inspection |  | 28 | New Finding (4th FUI): Doors in the means of egress do not have the required minimum width. (Available Width: 2'10" ) Location: 2nd floor east stair of fatory building. | For Interim & New building, Doors in a means of egress shall have a minimum width of 1 m (39 in.). in accordance with section 6.5.6.1 of RSC Technical Guidelines (Standard)¹ V1.0. | In Progress | Jan 10 2026 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 10-Dec-25: New Finding. | Within 1 Month | In Progress
Follow Up Inspection |  | 29 | New Finding (4th FUI): Aisles were found missing on several locations throughout the building. Location: Ground floor of factory building and shed 1. | Provide minimum aisle widths of 36-in. Aisles mark shall be clearly visible. | In Progress | Jan 10 2026 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 10-Dec-25: New Finding. | Within 1 Month | In Progress
Follow Up Inspection |  | 30 | New Finding (4th FUI): Liquefied or compressed gas cylinders were located within the factory on ground floor east side without adequate fire separation. Location: Boiler and CNG Room. | Remove the liquefied or compressed flammable gas cylinders. The storage or use of liquefied or compressed flammable gas (LPG/CNG) cylinders within the factory building as per section 3.4.2.1.11 of RSC Technical Guidelines (Standard)¹ V1.0. Or, Factory shall follow the requirements RSC Published "SUPPLEMENTARY PAPER ON TECHNICAL GUIDANCE NOTE FOR USE OF LIQUIFIED OR COMPRESSED FLAMMABLE GAS IN FACTORY PREMISES" to use or store liquefied or compressed flammable gas cylinders in the factory premises. | In Progress | Mar 10 2026 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 10-Dec-25: New Finding. | Within 3 Months | In Progress
Follow Up Inspection |  | 31 | New Finding (4th FUI): Sliding doors have provided along means of egress. Location: Store at shed 1. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. All doors in a means of egress shall be of the side‐hinged swinging type. Roll-­down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | In Progress | Jan 10 2026 | RPO Comments: On 03/03/2026 - The corrective action plan should be completed as per the given recommendation with immediate concern. On 10-Dec-25: New Finding. | Within 1 Month | In Progress

## Electrical
Date
06-Jul-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Lakhsma Innerwear Ltd, South vangnahati, Sreepur, Gazipur, Gazipur
Date of Inspection |  | 2018-11-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord/ Electrical SLD must be updated properly when electrical system is modified/ | Corrected | Feb 2 2019 | RPO Comments: On 14/12/2025 - The design documents (SLD) have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. On 11/09/2019: Not Corrected. SLD has been submitted to Accord for review. On 01/01/2023: Not Corrected. SLD got acceptance from RSC on 20-Jan-2021. Mismatch (BBT layout, Circuit breaker, load) observed with the accepted SLD. On 01/08/2023: Not Corrected. Accepted SLD is not matching on field due to changes of several areas. Factory needs to resubmit the SLD to RSC for review. On 14/03/2024: Not Corrected. Significant improvement (approx 50%) has been observed. Factory got Accepted SLD from RSC on 13th March 2024. On 20/10/2024: Neutral identification not completed for a few DBS. Load (e.g. Iron, Spreader, Sewing) KW rating is not mentioned as per nameplate rating. Load identification (e.g. EXF) is not started yet. TOB identification (all BBT) is not started yet. Individual overload protection is not found for sewing machine (all), Iron machine(all). Higher set point of ACCB & MCCB is observed in the LT Panel and MDB-01,GF | 2 Months | Pending Verification
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC)/ | Factory has to design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40)/ Once a LPS is designed properly, installation must be done accordingly/ | Corrected | Mar 2 2019 | On 11/09/2019: Not Corrected. Wrong installation and improper metal bond. On 01/01/2023: Not Corrected. Air terminal is not placed at required height, bi-metallic joint missing, LPS drawing need some modification.) On 01/08/2023: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Safety program is initiated but has no influence in the factory | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded/ Training must have an impact on the safety attitude of the personnel. | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. There is no influence of the training and LOTO device was not found. On 01/01/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued/ | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year/ If the operation of transformer is 24/7 in the facility twice in a year is a better practice/ | Corrected | Jan 2 2019 | On 11/09/2019: Corrected | 1 Month | Corrected
Initial Inspection |  | 5 | Inadequate working clearance around the transformer/s | Working clearance around each transformer shall be 1/07m/ If multiple transformers are installed, then the gap between two transformers must not be less than 1 m/ | Corrected | Mar 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Not Corrected. Work has been started but not finished yet. Also uneven height of cable trench observed around transformer. On 01/08/2023: Corrected. | 3 Months | Corrected
Initial Inspection |  | 6 | No working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear) | A working separation between LT and HT must be ensured/ A brick wall will do it; and adequate working clearance (1/07m) and ventilation must be ensured/ | Corrected | Mar 2 2019 | On 11/09/2019: Corrected | 3 Months | Corrected
Initial Inspection |  | 7 | 11kV power cable dropping from overhead line is not properly supported with pole and unprotected at the bottom of pole/ | 11kV distribution power cable must be fixed with pole properly and protected at the bottom avoiding any kind of physical injury/ | Done | Feb 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. | 2 Months | Corrected
Initial Inspection |  | 8 | Transformer Breather oil cup is empty | Transformer breather oil cup must be filled up to the oil mark on the cup/ | Corrected | Jan 2 2019 | On 11/09/2019: Corrected | 1 Month | Corrected
Initial Inspection |  | 9 | Oil level in transformer conservator oil tank is below minimum level/ | Minimum oil level in transformer conservator oil tank must be maintained, and it shall be checked periodically/ | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. Oil level wasn't identifiable. On 01/01/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 10 | Substation room has inadequate ventilation | Adequate ventilation must be maintained in sub-station room/ Cross/forced ventilation must be ensured/ | Done | Feb 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Phase barrier/separators are missing in MCCBs and link bus bar are not insulated/ | Phases must be separated by insulator (a rubber type no-flammable material shall be used for it) | Corrected | Feb 2 2019 | On 11/09/2019: Corrected. | 2 Months | Corrected
Initial Inspection |  | 12 | Generator output cables (laid on floor) are not protected and supported | Service cables from generator must be supported at its own breaker's terminal and with cable tray/ | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. Cables are not protected and cable tray installation has become a cause of fall hazard. On 01/01/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Power cable is buried in the concrete floor | Power cables must not be buried in the concrete/ A cable trench shall be constructed or routing power cables/ | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 14 | Power cables inside cable trench are buried by sand/soil/ | Power cables should not be buried directly in any case/ If it is not designed through sand/soil, removal of sand/soil must be done/ | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. | 1 Month | Corrected
Initial Inspection |  | 15 | Hot Spots were observed at several points/ | Hot spots must be eliminated from entire electrical system and shall be always carried forward | Done | Jan 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. No hot spot found during inspection. | 1 Month | Corrected
Initial Inspection |  | 16 | Circuit is drawn from bus bar without any protective means | Each electrical circuit must be drawn from distribution board bus bar using a proper type protection arrangement (MCCB/MCB) | Corrected | Feb 2 2019 | On 04/08/2019 the factory is asking timeline till 08/10/2019, which is not accepted/ Corrective action plan should be completed as per Accord's recommendation with immediate concern/ On 11/09/2019: Corrected | 2 Months | Corrected
Initial Inspection |  | 17 | Earth pits are not identifiable | Each earth pit shall be properly identifiable and marked for periodic maintenance | Done | Feb 2 2019 | On 11/09/2019: Not Corrected. On 01/01/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) | Corrected | Nov 1 2019 | On 01/01/2023: Not Corrected. Still found at few places. On 01/08/2023: Corrected. Loop connection found at few places. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Electrical distribution box/panels are full of fluffs (lint/dirt) | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. | Corrected | Nov 1 2019 | On 01/01/2023: Not Corrected. Panels & Tap-off boxes are not sealed properly. On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Earth Pit resistance test record doesn't match with field | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly | Corrected | Nov 1 2019 | On 01/01/2023: Not Corrected. ER test for LPS pits is not available. On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Feb 15 2023 | On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 22 | New Finding: Non rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | Corrected | Feb 15 2023 | RPO Comments: On 11/02/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 01/08/2023: Not Corrected. Still found at few areas. On 14/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 23 | New Finding: Transformer Silica gel is discolored | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | Corrected | Feb 15 2023 | On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 24 | New Finding: Lighting circuits and 3-pin sockets/ Machine are not separated in the electrical system | Lighting circuits and 3-pin sockets/ Machine shall be installed separately (should have no interconnections) | Corrected | Feb 15 2023 | On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | Corrected | Feb 15 2023 | On 01/08/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Sep 10 2023 | RPO Comments: On 11/07/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. 14/03/2024: Not Corrected. During inspection, all cables were not covered & few cables information mismatches found in the report. On 20/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Safety program is initiated but has no influence in the factory all electrical personnel. | Electrical safety training and awareness program for all electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Sep 10 2023 | RPO Comments: On 11/02/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 14/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Periodicity of thermographic survey is not continued. | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | Corrected | Sep 10 2023 | RPO Comments: On 11/02/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 14/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC) (LPS not installed in godown & mosques shed and bi-metallic joint need to do properly). | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | Corrected | Apr 24 2024 | RPO Comments: On 14/12/2025 - The design documents (SLD) have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. On 20/10/2024: Lightning Protection System (LPS) is not installed in godown & mosque shed. Bi-metallic joint is not found for dissimilar material in the dining shed. Air terminal missing in the Sewing shed. One-way connection is provided for air terminal in the main building, water tank area. | 2 Months | Pending Verification
Follow Up Inspection |  | 30 | New Finding: Earth Pit resistance (LPS) test record doesn't match with field (Actual LPS pit quantity- 17 Nos, tested quantity-12 Nos) | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly. | Corrected | Apr 24 2024 | RPO Comments: On 11/07/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 20/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Hot spots have been observed at some points. (above 40ºC of ambient) | Hot spots must be eliminated from entire electrical system. | Corrected | Mar 31 2024 | RPO Comments: On 11/07/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 20/10/2024: Corrected. | 1 Week | Corrected
Follow Up Inspection |  | 32 | New Finding: Heat shields/blankets missing to protect component and operator from excessive heat. | Heat shields/blankets must be installed to shield hot surface to protect component and operator from excessive heat. Proper guards shall be provided after shielding hot surface. Blankets on exhaust manifold, turbocharger housing and other engine components is not necessary. Suggested to consult with the generator supplier/service provider/expert before doing the job. | Corrected | Apr 24 2024 | RPO Comments: On 11/07/2024 - The factory management reported the remediation completion. This item will be verified in the next inspection. On 20/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: PVC and flexible pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected | Apr 24 2024 | RPO Comments: On 14/12/2025 - The design documents (SLD) have been reviewed and accepted by RSC. The factory management reported the remediation completion. This item will be verified in the next inspection. On 20/10/2024: Not Corrected. The issue still exists in the goddown. | 1 Month | Pending Verification

## Boiler
Date
06-Jul-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Lakhsma Innerwear Ltd, South vangnahati, Sreepur, Gazipur, Gazipur
Date of Inspection |  | 2022-01-25
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9589 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work status could not be assessed, as no image was provided. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 9589 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9589 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | In process | Aug 2 2025 | Comments on 15-Jul-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 4 | BB 9589 | Steam line connection is not terminated properly. | Any unprotective steam line shall be terminated in an appropriate manner that does not create any possibility of burn hazard for the operator (s). | Competed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work status could not be assessed, as no image was provided. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 5 | BB 9589 | Direct groundwater was used as feed water for the boiler. | Boiler feed water shall be treated. The feedwater and boiler water quality should meet the manufacturer's specifications. When unavailable, should meet manufacturer's standard or BS EN 12953-10. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 9589 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 9589 | The water level gauge glass was not protected. | The water level gauge glass should be properly protected with guard rods or covered by suitable protection housing. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 9589 | Inconsistency was observed between the boiler operator certificate data & CIoB website data regarding all the operator’s personal information. | Boiler operator certificate data should match with the CIoB website data for a particular certificate number & class. | In process | Jul 16 2025 | Comments on 15-Jul-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 WEEKS | In Progress
Initial Inspection | External visual inspection | 9 | BB 14808 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: As per the pictorial evidence, the issue is not remediated yet. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 14808 | Necessary technical documents (Piping and Instrumentation diagram, commissioning documents, water treatment design and calculation, flue gas analysis report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Completed | Sep 2 2025 | Comments on 15-Jul-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 14808 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | In process | Aug 2 2025 | Comments on 15-Jul-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 1 MONTH | In Progress