## Structural
Date
15-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mahadi Fashion (Pvt.) Ltd., Basugaon, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2015-02-08
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Discrepancy between site observation and information on drawing | Factory Engineer to prepare a set of “as-constructed” drawings to reflect the actual column dimensions and water tank location. | Done: As built drawing already finished but last follow up inspection accord inspector have some re-commendations and we already rectified as per accord recommendations. | Jan 30 2016 | ON 02/09/2015: No as built drawing was provided at the time of inspection. ON 27/03/2017: During inspection, A set of As- Built drawing was observed which was not corrected as per observation of initial report. Factory is required to prepare As-Built drawings with necessary correction as per initial report and submit to ACCORD. ON 07/06/2017: No as-built drawing has been prepared yet. They shall submit the EA to ACCORD as soon as possible. On 18/02/2018: Factory submitted EA to ACCORD on 12 Feb 2018 and review comments were sent on 18-Feb-2018. Re-submission is required with some corrections. Factory will submit EA along with as-built drawings to ACCORD. On 22-07-2018: Factory prepared as-built drawing for the building and got acceptance from ACCORD along with the EA report. Due to find some discrepancies during the verification inspection, factory is required to revise the as-built drawing and submit to ACCORD within 7days after receiving the report. On 17/12/2018: As-built drawing had been prepared as a part of EA report. Factory management got EA re-acceptance from ACCORD on 27/11/2018. On 08-Jan-2023: Corrected from previous inspection. As-built drawings have been prepared and accepted by the Accord. On 18-Jun-2025: Corrected previously. | within 6-months | Corrected
Initial Inspection |  | 2 | Apparently Non engineered Roof structures | Building engineer to check the capacity of the lightweight roof structures and make any necessary alterations. | Already done | Jan 30 2016 | ON 02/09/2015: The capacity of the non engineered roof structures was not checked to find it's adequacy against lateral and vertical load. ON 27/03/2017:The capacity of the non-engineered roof structures has not been checked yet. Building Engineer is required to check the capacity of the non- engineered roof structures against lateral and vertical loads and submit the assessment to ACCORD as soon as possible. ON 07/06/2017: Factory shall check the capacity of the lightweight roof structures and submit it as part of EA to ACCORD as soon as possible. On 18/02/2018: Factory submitted EA to ACCORD on 12-Feb-2018 and review comments were sent on 18-Feb-2018. Re-submission is required with some corrections. Factory will submit EA along with lightweight roof capacity calculations to ACCORD. On 22-07-2018: The retrofitting works were ongoing till the inspection day. However, some mismatches were found in as-built drawing and onsite condition. Factory is required to revise the drawing and report and submit to ACCORD within 7days after receiving the report. On 17/12/2018: Factory management got EA re-acceptance from ACCORD on 27/11/2018. As per EA recommendation retrofitting works were found completed. On 08-Jan-2023: Corrected from previous inspection. Non-engineered staircase roof has been replaced with concrete roof. On 18-Jun-2025: Corrected previously. | within 6-months | Corrected
Follow Up Inspection |  | 3 | No edge protection is provided at top of the stair roof. | No edge protection is provided at top of the stair roof will be ensured. | done | Jan 30 2016 | ON 02/09/2015: It is required to provide edge protection around that zone so that no mishap can take place. ON 27/03/2017: Factory has provided edge protection at top of the stair roof to avoid falling hazard. ON 07/06/2017: This issue has been corrected as per 2nd follow up inspection and found same. On 18/02/2018: This issue has been corrected previously. On inspection, edge protection was found in place. On 22-07-2018: The issue is corrected as per previous inspection. On 17/12/2018: Corrected in previous follow up inspection. During inspection edge protection was found on roof top. On 08-Jan-2023: Corrected from previous inspection. Railing has been provided at roof. On 18-Jun-2025: Corrected previously. | within 6-months | Corrected
Follow Up Inspection |  | 4 | New finding-1: A newly constructed dinning shed observed. | Building engineer is required to check the stability of the shed against lateral and vertical loads | Done: Retrofitting work already finished but last follow up inspection accord inspector have some re-commendations and we already rectified as per accord recommendations. | May 8 2017 | ON 27/03/2017: During inspection, A newly constructed dining shed observed on the factory premises which seems to be non-engineered. Building Engineer is required to check the stability of the shed against lateral & vertical load and submit the assessment to ACCORD as soon as possible. ON 07/06/2017: Factory management shall submit the EA report to ACCORD as soon as possible. On 18/02/2018: Factory submitted EA to ACCORD on 12-Feb-2018 and review comments were sent on 18-Feb-2018. Resubmission of EA report is required with some corrections. Factory will soon submit EA report to ACCORD. On 22-07-2018: The retrofitting works were ongoing till the inspection day. However, some mismatches were found in as-built drawing and onsite condition. Factory is required to revise the drawing and report and submit to ACCORD within 7days after receiving the report. On 17/12/2018: Factory management got EA re-acceptance from ACCORD on 27/11/2018. As per EA recommendation retrofitting works were found completed. On 08-Jan-2023: Corrected from previous inspection. Remedial works of dining shed and accessories store shed have been completed as per Accord accepted EA. On 18-Jun-2025: Corrected previously. | within 6-months | Corrected
Follow Up Inspection |  | 5 | New finding-2: Exposed rebar at the rooftop of Main Production Building | Remove the corrosion and apply suitable corrosion resistance coating on the exposed rebar. | Already done | Feb 20 2023 | .On 08-Jan-2023: Exposed rebar observed at roof of the Main Production Building. The factory is required to remove the corrosion and apply suitable corrosion resistance coating on the exposed rebar. On 18-Jun-2025: The factory applied anti-rust proof paint on exposed rebar. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 6 | New finding-3: Heavy loading on the top slab of underground water reservoir (UGWR) of the new Fire Pump Building. | The building engineer is required to check the adequacy of the UGWR as part of Engineering Assessment (EA) and submit EA documents to the RSC for review. | We are working according to the report's review. | Feb 20 2023 | On 08-Jan-2023: Design documents were not available for the new Fire Pump Building. Heavy vehicle loading observed on the top slab of under ground water reservoir (UGWR) portion of the building. The building engineer is required to carry out Engineering Assessment (EA) of the structure and submit to RSC for review. On 18-Jun-2025: The building engineer was required to prepare and submit the EA for the Fire Hydrant Building within 28-Jan-2025. But till the date of inspection, the factory has not submitted the EA to RSC. RPO Comments: 14-Mar-2026:Factory is working on this cap issue and they are required to complete the issue before next follow up inspection. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 7 | New finding-4: Lack of design documents for the new Fire Pump Building. | Carry out remedial works as per RSC accepted EA if required. | We are working according to the report's review. | Jul 10 2023 | On 08-Jan-2023: Once the EA is accepted by the RSC, carry out remedial works within mentioned timeline. On 18-Jun-2025: The factory is required to complete all remedial works after getting acceptance from RSC if required. RPO Comments: 14-Mar-2026:Factory is working on this cap issue and they are required to complete the issue before next follow up inspection. | (within 6 months) | In Progress
Follow Up Inspection |  | 8 | New finding-5: Undocumented structures (Dining Shed extensions, Parking Shed, Guard Room and Canopy Shed) observed in the factory premises. | The building engineer is required to prepare design documents and submit to RSC for review. | We are working according to the report's review. | Feb 20 2023 | On 08-Jan-2023: Undocumented single story structures (Dining Shed extensions both side of existing dining shed, Parking Shed near fire pump building, Guard Room at entrance and Canopy Shed adjacent to generator Shed) observed in the factory premises. The building engineer is required to prepare design report for Dining Shed Extensions & Canopy Shed and as-built drawings for the other structures. Submit all the documents to RSC for review. On 18-Jun-2025: The building engineer was required to prepare and submit the design report for Dining Shed Extensions, Canopy Shed, and as-built drawings for the other structures within 28-Jan-2025. But till the date of inspection, the factory has not submitted the Design Report to RSC. RPO Comments: 14-Mar-2026:Factory is working on this cap issue and they are required to complete the issue before next follow up inspection. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 9 | New finding-6: Undocumented structures (Dining Shed extensions, Parking Shed, Guard Room and Canopy Shed) observed in the factory premises. | Carry out remedial works as per RSC accepted EA where required. | We are working according to the report's review. | Jul 10 2023 | On 08-Jan-2023: Once the design documents is accepted by the RSC, carry out remedial works within mentioned timeline. On 18-Jun-2025: The factory is required to complete all remedial works after getting acceptance from RSC if required. RPO Comments: 14-Mar-2026:Factory is working on this cap issue and they are required to complete the issue before next follow up inspection. | (within 6 months) | In Progress
Follow Up Inspection |  | 10 | New finding-7: Water ponding on the roof of the Main Production Building. | The building engineer is required to improve the drainage system on the roof with an adequate slope. | We are working according to the report's review. | Dec 31 2025 | On 18-Jun-2025: During inspection, water ponding was found on the roof of the Main Production Building. The building engineer is required to improve the drainage system on the roof with an adequate slope. RPO Comments: 14-Mar-2026:Factory is working on this cap issue and they are required to complete the issue before next follow up inspection. | (within 6 months) | In Progress

## Fire
Date
15-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mahadi Fashion (Pvt.) Ltd., Basugaon, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2015-02-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Unsealed electrical shafts are located in the fire-rated floor/ceiling assemblies at northeast corner. | Provide a minimum 2-hr fire- rated shaft to separate the utility risers from each floor level and seal all penetrations in floor/ceiling assemblies to maintain the fire separation. | done | May 5 2016 | On 27/03/2017: Corrected in 5th follow up. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Rooms used for combustible storage are not separated by fire-rated construction on the ground floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | done | Jun 10 2016 | On 07/06/2017: The factory has installed fire doors in bonded wear house. But door coordinators has not been found in double leaf fire doors. On 18/12/2017: Corrected. Factory has installed fire door in store room and interfaced with FACP and door accessories (door coordinator in double leaf, door closer, panic bar etc.) were working properly during follow up inspection. On 02/07/2018: Corrected based on previous follow up. Only ground floor store is separated. On 21/11/2018: Corrected based on previous follow up. Only ground floor store is separated. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | The empty elevator shafts does not have the proper fire rated construction on each floor. | Provide the proper 2 hr. fire rating for the shaft and 1.5 hr. fire rating for the elevator door. | done | Apr 13 2016 | On 07-02-16: Partially corrected. The factory need to cover the shaft. On 13-04-16: Corrected. Elevator shaft doors have been sealed. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | The exit stair enclosures are not separated from work areas on each floor by fire-rated construction. | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2-hr fire resistance rating for buildings 4 or more stories. Provide minimum 1.5-hr fire rated doors for buildings that are 4 or more stories. Ensure that the fire doors are self-closing and positive latching and they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | done | Jun 10 2016 | On 07/06/2017: Not corrected yet. Fire doors have been installed in all floors. But stair is not separated from ground floor. Moreover, door coordinators were missing in fire doors and few doors have been found blocking the stair landings. On 18/12/2017: Corrected. Factory has installed fire door at exit and interfaced with FACP and door accessories (door coordinator in double leaf, door closer, panic bar etc.) were working properly during follow up inspection. On 02/07/2018: Corrected as on previous follow up. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | The northeast exit stair is not separated from maintenance room on the 2nd floor by firerated construction. | Provide minimum 2-hr fire rated construction wall. Seal all unprotected openings to separate the exit stairs from other building spaces on all floor levels. | done | Jun 10 2016 | On 07/06/2017: Corrected. Fire door has been installed in maintenance room and fire door has been found closed during follow-up inspection. Note: If the factory wants to keep the fire door open, they will require to install automatic door holder interfacing with FACP. On 18/12/2017: Corrected as per last follow up. On 02/07/2018: Corrected as on previous follow ups. Openings shall be sealed up to 10ft distance from covered roof at N-E building exit. On 21/11/2018: Corrected as on previous follow ups. Openings has been sealed after inspection confirmed by pictorial evidence mail . On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Egress doors and gates with locking features are provided at building exits, along egress routes and exit discharge. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101 and ACCORD standard 6.8.2. | done | Apr 13 2016 | On 07/06/2017: Corrected as per previous follow-up. On 18/12/2017: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. On 02/07/2018: Corrected based on previous follow ups. Note: Non-compliant lock was found in finished goods store and that was removed instantly also factory conforms that further it will not used in the factory. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 7 | Building did not have stair designation signs and occupant load signs at required locations. | Provide stair designation signs and occupant load signs at required locations. | done | Apr 13 2016 | On 27/03/2017: Corrected as on 3rd follow up. On 07/06/2017: Corrected. On 18/12/2017: Corrected as per previous follow up. Note: Factory shall update stair designation sign. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Initial Inspection |  | 8 | Collapsible gates and sliding doors are provided at building exits, along egress routes and exit discharge. | Replace all gates and sliding doors along the means of egress with side-hinged, swinging egress doors in accordance with ACCORD standard 6.8.1. | done | Apr 13 2016 | On 27/03/2017: Corrected in 3rd follow up. On 07/06/2017: Corrected. On 18/12/2017: Corrected. During follow up inspection non-compliant doors/gates were not found in egress routes. On 02/07/2018: Corrected based on previous follow ups. Note: Non-compliant glass sliding door was found in sample section, it shall be removed. On 21/11/2018: Non-compliant glass sliding door still present at sample section and embroidery section. Refer to issue 40. On 28/08/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | Exit stairs serve more than 5 stories and do not have required reentry provisions. | Every door in a stair enclosure serving more than 5 stories shall be provided with re-entry unless it meets ACCORD standard 6.8.3.1. | done | Jun 10 2016 | On 27/03/2017: It is an integrated part of fire door installation. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Handrails are not provided on both sides of the exit stair. | Provide handrails on both sides of the exit stair. New handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Intermediate handrails shall be provided when the stair width exceeds 2.2 m (87 in.) | done | Apr 13 2016 | On 27/03/2017: Corrected as on 3rd follow up. Shall be installed on 6th floor. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | Southwest and northwest exit stairs discharge inside the building on the ground floor. | Modify stair to discharge directly outside or Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). | done | Jun 10 2016 | On 12/12/2016: Only L/C has been opened for fire door. On 27/03/2017: Civil work is going on. On 07/06/2017: Not corrected yet. On 18/12/2017: Corrected. Factory has installed fire door in store room & interfaced with FACP by electro-magnetic door holder device. On 02/07/2018: Corrected based on previous follow up. Stair lobby shall not be used for any purpose and factory shall aware the workers as well as staffs. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 12 | The fire alarm system is antiquated, not a listed system and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | We are working as per the report (FADS-1st Review) | Jul 10 2016 | On 18/12/2017: During follow up inspection (testing & commissioning) resistor was fixed inside FACP, alarm level was found less than 15dB compared with ambient sound, ground fault not found & manufacturing date was missing in battery. However, fire alarm system was not functional properly. As built drawing was not as per actual site condition. On 02/07/2018: T&C comments (not limited to): In some areas device address is not clearly marked, inadequate audibility even not audible in generator room and store room, detector coverage area not comply with standard (isolated room, spacing and pitched roof), MCP is missing in some required locations/areas, some devices are found without support and protection. All the deficiencies shall be remediated as soon as possible as per NFPA 72 prior to acceptance test again. On 21/11/2018: T&C observations (not limited to): Schematic diagram is not posted in FACP room, AC power source is not dedicated, NAC power extended battery calculation was not found (factory emailed document need to onsite verification), NAC extender panel grounding shall be proper, NAC circuit/wiring is not proper, wiring of fire alarm device found exposed at some location/areas, some device address is not clearly marked/ not visible, alarm sound level shall be 15dB higher compared with ambient sound, some device not properly supported. All the deficiencies shall be remediated as soon as possible and system shall comply with NFPA 72 prior to acceptance test again. On 09/09/2019: Reportedly, modification work completed. Factory will submit T&C docx soon for T&C VI. On 26/06/2024: After modification work, documentation and drawings, the system needs pre-T&C again on site. See details in Pre-T&C report. On 28/08/2024: The factory is planning to start the modification work of fire alarm and detection system as per the last Pre-T&CVI report. RPO Comments:On 14-March-2026: Factory is required to complete the issue before next follow up inspection. | Design within 4 months, install within 9 months | In Progress
Initial Inspection |  | 13 | The required no smoking signs are not present in the factory. | Smoking is prohibited in any garment factory building or separate storage building. Signs shall be posted in Bengali and English at all building entrances. If the factory creates a designated smoking area outside the building, information of these areas will be posted on the signs. | done | Apr 13 2016 | On 12/12/2016: Corrected in 1st follow up. On 27/03/2017: Corrected in 1st follow up. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 1 months | Corrected
Initial Inspection |  | 14 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | done | Apr 13 2016 | On 27/03/2017: Corrected in 3rd follow up. On 07/06/2017: Corrected. On 18/12/2017: Corrected as per previous follow-up. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72. | done | Jul 10 2016 | On 07/06/2017: It is an integrated part of fire alarm system. On 18/12/2017: Corrected. On 02/07/2018: Corrected as on previous follow up. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Fire department connection is not provided. | Provide fire department connection in accordance with ACCORD standard 5.5.4. | Already done | Jul 25 2016 | On 27/03/2017: It is an integrated part of fire fighting system. On 07/06/2017: It is an integrated part of fire fighting system. On 18/12/2017: It is an integrated part of standpipe system. On 02/07/2018: It is an integrated part of standpipe system. On 21/11/2018: Corrected. Listed FDC has been provided after inspection confirmed by pictorial evidence mail .. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 17 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 20. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 20. | Already done | Jul 25 2016 | On 27/03/2017: It is an integrated part of fire fighting system. On 07/06/2017: It is an integrated part of fire fighting system. On 18/12/2017: It is an integrated part of standpipe system. On 02/07/2018: It is an integrated part of standpipe system. On 21/11/2018: Corrected. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 18 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 14. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 14. | Already done | Jul 25 2016 | On 12/12/2016: It is an integrated part of fire fighting system. On 27/03/2017: It is an integrated part of fire fighting system. On 07/06/2017: It is an integrated part of fire fighting system. On 18/12/2017: No action has been taken yet. On 02/07/2018: It is an integrated part of standpipe system. On 21/11/2018: Corrected. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 19 | Visible and audible notification was not provided for the building in accordance with NFPA 72. | Provide visible and audible notification for the building in accordance with NFPA 72. | Fire alarm system already installation finished. But during the 9th follow up have some re-commend but already we have rectified as per accord requirement and we are offering for T&C to the accord. | Jul 10 2016 | On 27/03/2017: It is an integrated part of fire alarm system. On 07/06/2017: It is an integrated part of fire alarm system. On 18/12/2017: During follow up inspection (testing & commissioning) of fire alarm system was not functional properly. On 02/07/2018: Corrected. On 21/11/2018: Corrected as on previous follow up. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 20 | Fire pump is not provided in accordance with ACCORD standard 5.5.1 and 5.5.1.1. | Provide a new fire pump that meets ACCORD standard 5.5. | We are working as per the report (FADS-1st Review) | Jul 25 2016 | On 18/12/2017: It is an integrated part of standpipe system. On 02/07/2018: Pump set has been in-housed, pump room construction is going on. On 21/11/2018: T&C observations (not limited to): No drainage system in pump room, provided reducer is concentric type, rubber pipe is used for fuel tank connection, fuel tank has no level gauge, provided certificate is not match with installed pumps, pump listing tag/label is manipulated (actually installed pump is horizontal split case but mane plate/tag shows its end suction pump), flow switch is not provided in standpipe riser, no suction and discharge pressure gauge, pressure setting is not proper, a control valve is not supervised in pump room, pump performance is not up to the mark/standard, interfacing/supervision is not proper, filling of UGWR is not automatic, class-l landing valves has no coupling converter. All the deficiencies shall be remediated as soon as possible as per NFPA 13, 14, 20 and 22 prior to acceptance test again. On 09/09/2019: Reportedly, modification work completed. Factory will submit T&C docx soon for T&C VI. On 26/06/2024: After modification work, documentation and drawings, the system needs pre-T&C again on site. See details in Pre-T&C report. On 28/08/2024: The factory has started the modification work of Standpipe System as per the last Pre-T&CVI report. RPO Comments:On 14-March-2026: Factory is required to complete the issue before next follow up inspection. | Within 6 months | In Progress
Initial Inspection |  | 21 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the building, tied into the fire alarm system, in accordance with NFPA 72. | Fire alarm system already installation finished. But during the 9th follow up have some re-commend but already we have rectified as per accord requirement and we are offering for T&C to the accord. | Jul 10 2016 | On 27/03/2017: It is an integrated part of fire alarm system. On 07/06/2017: It is an integrated part of fire alarm system. On 18/12/2017: During follow up inspection (testing & commissioning) of fire alarm system was not functional properly. On 02/07/2018: Corrected. On 21/11/2018: Corrected as on previous follow up. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 22 | The required standpipe system is not provided for the building in accordance with the ACCORD standard. | Install a new standpipe system in accordance with ACCORD standard 5.4 and NFPA 14. A class III system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more. A class I system shall be permitted in buildings protected throughout by an approved automatic sprinkler system. | We are working as per the report (FADS-1st Review) | Jul 25 2016 | On 27/03/2017: Found same as previous follow up. On 07/06/2017: No action has been taken yet for installation of the system. The factory has informed that they will open L/C within one month. On 18/12/2017: Standpipe system drawing has been reviewed by Accord. Still no action has been taken yet for materials purchase. On 02/07/2018: Pump set has been in-housed, pump room construction is going on. On 21/11/2018: Refer to issue 20 (for comments). On 09/09/2019: Reportedly, modification work completed. Factory will submit T&C docx soon for T&C VI. On 26/06/2024: After modification work, documentation and drawings, the system needs pre-T&C again on site. See details in Pre-T&C report. On 28/08/2024: The factory has started the modification work of standpipe system as per the last Pre-T&CVI report. RPO Comments:On 14-March-2026: Factory is required to complete the issue before next follow up inspection. | Within 6 months | In Progress
Initial Inspection |  | 23 | Manual on-off switch is provided for emergency lighting units on each floor and each stair. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | done | Apr 13 2016 | On 27/03/2017: Corrected in as on 3rd follow up. On 07/06/2017: Corrected as per previous follow-ups. On 18/12/2017: Corrected. Not found. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 24 | Inspection, testing and maintenance for the emergency lighting system was not in accordance with The accord satandard. | Inspection, test and maintain the emergency lighting system in the accordance with the Accord standard. | done | Apr 13 2016 | On 07/06/2017: Corrected. On 18/12/2017: Corrected as per previous follow up. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 3 month | Corrected
Follow Up Inspection |  | 25 | New Finding: The generator and sub station rooms are not seperated by fire rated construction(opening, penetration. | Separate the generator and sub station rooms by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain the required fire separatios. | Already done | Jun 10 2016 | On 07/06/2017: Not corrected yet. Unsealed openings have still found in generator room. On 18/12/2017: Corrected. Factory has sealed penetrations. On 02/07/2018: Re-opened. Separation wall is not constructed up to the roof. Note: Diesel store kept open in front of generator room and building exit which was removed instantly. On 21/11/2018: Corrected. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Apr 7 2016 | Corrected
Follow Up Inspection |  | 26 | New Finding: The gas cylinder and boiler rooms are not seperated by fire rated construction. | Separate the gas cylinder and boiler rooms by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain the required fire separations. | done | Jun 10 2016 | On 07/06/2017: Work is in progress. On 18/12/2017: Not corrected. Factory shall separate CNG cylinders as per Accord recommendation. On 02/07/2018: Corrected. Separation is completed as per Accord recommendation. On 21/11/2018: Corrected as on previous follow up. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | May 7 2016 | Corrected
Follow Up Inspection |  | 27 | New Finding: Emergency lights on every floor is indaquate. | Provide adequate emergency lights to illuminate the egress paths and aisles properly at every floor. | Already done | May 7 2016 | On 07/06/2017: Corrected. On 18/12/2017: Corrected. Note: Factory shall ensure that emergency light illumination level on aisles are adequate. On 02/07/2018: Corrected based on previous follow ups. Shall be provided in storage rooms with protected cover. On 21/11/2018: Re-opened. Emergency light not provided in storage rooms and several exit signage units were found burnt/non-illuminated. On 09/09/2019: Emergency light provided at store. On 28/08/2024: Corrected. | May 7 2016 | Corrected
Follow Up Inspection |  | 28 | New Finding: The width of the exit stair is less than 36 Inches. | provide minimum 36 inches width of the exit stair | done | May 7 2016 | On 02-08-16: Corrected. Factory has a total of 4 staircases. The said staircase shall be in use but NOT as an emergency exit. Remaining 3 stairs are sufficient for exit considering the occupancy. Factory is required to fully separate ALL staircases (including this one) from adjacent production spaces with fire rated construction. On 13.10.2016: Corrected. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected based on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. Note: As the factory has required exit considering the occupant load, the said staircase is not required to be an emergency exit. If factory declare as an emergency exit, recommendation shall meet. On 28/08/2024: Corrected. | May 7 2016 | Corrected
Follow Up Inspection |  | 29 | New Finding: Storage was locate in the exit stair. | Remove all storage from exit stair. | done | Apr 20 2016 | On 13-04-16: New Finding On 02-08-16: Corrected. All stairs should be storage free at all times. On 13.10.2016: Corrected. On 02/07/2018: Corrected as on previous follow ups. Room under N-W stair shall be removed and S-W stair lobby shall not be used for any purpose and factory shall create awareness to worker and staffs. On 21/11/2018: Corrected as on previous follow ups. Room under N-W stair has been sealed after inspection confirmed by pictorial evidence mail . On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | 42480 | Corrected
Follow Up Inspection |  | 30 | New Finding (4th Follow-up): During follow-up inspection, it was found that the empty elevator shafts does not have the proper fire rated construction on each floor. The elevator shaft is a vertical opening connecting all floors. | Provide the proper 2 hr. fire rating for the shaft and 1.5 hr. fire rating for the elevator door. Factory shall seal all openings between the shaft and the production floors with fire rated construction. | done | Sep 2 2016 | On 6.10.16: Factory is asking time till 31.12.16 which is not acceptable. On 02-08-16: New Finding On 07/06/2017: Corrected. On 18/12/2017: Corrected as per previous follow up. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 31 | New Finding (4th Follow-up): During Follow-up inspection, it was found that day-care/ medical rooms are not properly separated from accessories store with fire rated construction. | Provide a minimum 2-hr fire-rated separation between the day-care/ medical rooms and accessories store. | done | Sep 2 2016 | On 6.10.16: Factory is asking time till 30.04.17 which is not acceptable. On 02-08-16: New Finding On 07/06/2017: Corrected as per previous follow-ups. On 18/12/2017: Corrected as per previous follow up. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 32 | New Finding (4th Follow-up): During follow-up inspection areas used for combustible storage are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows:- Maximum height of 2.4m and maximum area of 23m2- If sprinkler protected: maximum height of 3.66m and maximum area of 93m2Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | We are working as per the report (FADS-1st Review) | Sep 2 2016 | On 19.02.17: Factory is asking time till 31.04.17 which is not acceptable. On 02-08-16: New Finding On 18/12/2017: During follow up inspection finished goods storage areas were not separate from work area on 1st floor. On 02/07/2018: Found same as previous follow up in 1st and 4th floor. Dedicated storage room should be provided in 4th floor considering total storage area. On 21/11/2018: Still 4th floor store is not separated by 2-hr fire rated construction. On 09/09/2019: Storage area reduced & maintaining in process storage properly with dedicated area marking. On 28/08/2024: Issue re-opened. Non-compliant open storage areas were observed on 1st and 4th floor during Follow-up inspection. RPO Comments:On 14-March-2026: Factory is required to complete the issue before next follow up inspection. | Within 1 month | In Progress
Follow Up Inspection |  | 33 | New Finding: Electrical panel is located inside the stairwell on ground floor. | Remove all electrical panels and all storage materials from stairwells. | Already done | Jan 12 2017 | On 27/03/2017: Corrected. Removed. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected based on previous follow ups. Panel was found and factory removed it instantly. On 21/11/2018: Re-opened. Electric panel box found in the same location which was previously removed. Factory is not maintaining safety concerns. On 09/09/2019: Corrected. On 28/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 34 | New Finding: Storage was located in the exit stair (Ground floor). | Remove all storage from exit stairs. | done | Dec 17 2016 | On 27/03/2017: Store room and finished goods store found at stair discharge at ground level. On 07/06/2017: Corrected. Removed. On 18/12/2017: Corrected. Not observed. On 02/07/2018: Corrected based on previous follow ups. IPS with battery storage was found and factory removed it instantly. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 35 | New Finding: The south west stair lobby at ground is used as loading and unloading area. | Immediately remove the storage materials and loading unloading | done | Dec 17 2016 | On 27/03/2017: Found almost same as before. Loading unloading area has been replaced by finished goods area. On 07/06/2017: Corrected. Loading unloading area has not been observed in the mentioned place. On 18/12/2017: Corrected as per last follow up. On 02/07/2018: Corrected based on previous follow ups. Work activity is not found during inspection. Stair lobby shall not be used for any purpose and factory shall aware the workers as well as staffs. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 36 | New Finding: Manual on-off switch is found in exit signage units | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Already done | Jan 12 2017 | On 27/03/2017: Corrected. Removed. On 07/06/2017: Corrected. On 18/12/2017: Corrected. Removed. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Re-opened. Exit signage units still has manual on/off switch's. On 09/09/2019: Removed as per site condition. On 28/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 37 | New Finding: Lots of emergency light not illuminated during testing (burned out, brocken etc)Location throughout the factory. | Regulary inspect all emergency lighting systems as per Accord standard and replace/install lights as needed to illuminate signs. | done | Dec 17 2016 | On 27/03/2017: Corrected. Shall be regularly and properly inspected. On 07/06/2017: Corrected. On 18/12/2017: Corrected. On 02/07/2018: Corrected based on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 38 | New Finding: Height of the parapet in occupiable roof was less than 42 inch. | Provide parapets or guards with a minimum height of 1067 mm (42 inch). | done | Jan 12 2017 | On 19.02.17: Factory is asking time till 30.03.17 which is not acceptable. On 27/03/2017: No action has been taken yet. On 07/06/2017: Corrected. On 18/12/2017: Corrected as per last follow up. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Within 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Occupant load sign was not provide. | provide occupant load signs at required locations. | done | Dec 17 2016 | On 19.02.17: Factory is asking time till 30.03.17 which is not acceptable. On 27/03/2017: Corrected. On 07/06/2017: Corrected. On 18/12/2017: Corrected. Posted. On 02/07/2018: Corrected as on previous follow ups. On 21/11/2018: Corrected as on previous follow ups. On 09/09/2019: Corrected as on previous follow ups. On 28/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 40 | New Finding: Sliding type doors have provided along means of egress [sample section and embroidery section]. | Replace all collapsible/sliding/shutter type doors & gates by the side‐hinged swinging type doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Already done. | Nov 25 2018 | On 09/09/2019: Sliding gate removed on mentioned area. On 28/08/2024: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 41 | New Finding: Unsealed penetrations and openings are located in exit stair enclosures. (Fire fighting hose box penetration at S-W, N-W & N-E stair and electrical cable trench/riser at S-W & N-W stair enclosures wall) | Remove all electric cable riser and/or trench and electrical pipes from the exit stair enclosures. Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. Penetrations into and through an exit enclosure shall be prohibited with the exception of required exit doors, sprinkler piping, standpipes, electrical raceway for fire alarm equipment, and electrical conduit serving the exit enclosure. | Already done. | Dec 21 2018 | On 09/09/2019: Corrected as per site condition. On 28/08/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 42 | New Finding (13th FUI): Unsealed Electrical riser penetrations and openings are located in the fire rated floor/ceiling assemblies on all floors of main factory building. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's datasheet. Or Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | We are working as per the report (FADS-1st Review) | Oct 30 2024 | On 28/08/2024: New Finding. RPO Comments:On 14-March-2026: Factory is required to complete the issue before next follow up inspection. | Within 2 months | In Progress

## Electrical
Date
15-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mahadi Fashion (Pvt.) Ltd., Basugaon, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2015-02-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Thermo graphic scanning of the entire electrical system has not been performed. | Thermo graphic scanning of the entire electrical system must be performed twice in a year. | Corrected | Oct 10 2015 | On 07/02/2016: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 2 | Electric safety program is not initiated. | Electrical safety training and awareness program for the electrical personnel and workers must be initiated and recorded. | Corrected | Jan 10 2015 | On 07/02/2016: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 3 | Factory does not have maintenance report. | Factory must keep accurate maintenance reports with all necessary equipment data. | Corrected | Feb 7 2016 | On 07/02/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 4 | Damaged PVC conduit. | Damaged PVC conduit should be replaced. Rigid pipes shall be used, clamped with saddle at regular interval (600 mm preferably). | Corrected | Sep 5 2015 | On 07/02/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 5 | Panel base plates removed to allow cable entry (typical). | Install panel base plate and provide appropriate cable gland. Ensure the cables are not stressed on the sharp edges, and install non-combustible covers if there is any gap remaining. | Corrected | Oct 13 2016 | On 07/02/2016: This issue is not done yet. New committed timeline is given till 31-3-16 to close the issue. On 13/04/16: Not corrected. New time line is given till 30/05/2016. On 02/08/2016: Still not corrected. On 13/10/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 6 | Oil cup below transformer breather is empty. | Breather oil cup must be filled with transformer oil to the required level as instructed by the manufacturer. | Corrected | Apr 30 2015 | On 02/09/2015: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 7 | HT cable laid over the LT cables. | Cables of different voltage levels must be separated in different trays. | Corrected | Oct 30 2015 | On 07/02/2016: Corrected. | IMMEDIATE | Corrected
Initial Inspection |  | 8 | Cable trenches are not protected. | Cable trenches must be covered with protective covers (concrete slabs or checkered plates) to prevent the cables from getting damaged. | Corrected | Jan 10 2015 | On 07/02/2016: Corrected. | 10 WEEKS | Corrected
Initial Inspection |  | 9 | Cables or wiring drawn in flexible PVC conduits, laid outside (building wall) without support. | Cables laid outside building must be supported in cable trays with cover and protected against weather and possible physical damages. | Corrected | Jan 10 2015 | On 07/02/2016: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 10 | Panel doors not connected with earth bond (typical). | All metal panel doors shall have earth connection by at least 4 rm earth cable. | Corrected | Jan 10 2015 | On 07/02/2016: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 11 | Transformer guarded with wire mesh fencing. | Construct a fire rated room for the transformer. Assign a qualified engineer to design a required transformer room according to BNBC, Section-2.6.3. | Corrected | Dec 31 2016 | On 07/02/2016: Not corrected. New committed timeline is given till 31-3-16 On 13/04/2016: Not corrected. Proper clearance around the transformer is not provided. New time line is given till 30/05/2016. On 02/08/2016: Not corrected. On 13/10/2016: Not corrected. On 12/12/2016: Not corrected. On 27/03/2017: Not corrected. On 07/06/2017: Not corrected. No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s . On 18/12/2017: Corrected. | 10 WEEKS | Corrected
Initial Inspection |  | 12 | Power cables laid on concrete floor. | Construct cable trench covered with checkered plate or covered cable trays to protect the cables from physical damage. | Corrected | Nov 6 2015 | On 02/09/2015: Corrected. | 10 WEEKS | Corrected
Initial Inspection |  | 13 | Cable passed through wall not protected. | Cable tray or conduit must be passed across the wall to support and protect the cables. The openings after the passage of cable tray or conduit should be sealed with the fire rated materials. | Corrected | May 30 2016 | On 07/02/2016: This issue is not done yet. New committed timeline is given till 31-3-16 to close the issue. On 13/04/2016: Not corrected. New time line is given till 30/05/2016. On 02/08/2016: Corrected. | 5 WEEKS | Corrected
Initial Inspection |  | 14 | Base plate not installed for the generator panel. | Panel base plates must be installed and cable(s) entering panel must be firmly fixed with cable gland. | Corrected | Mar 31 2016 | On 13/04/2016: Corrected. On 07/02/2016: This issue is not done yet. New committed timeline is given till 31-3-16 to close the issue. | 5 WEEKS | Corrected
Initial Inspection |  | 15 | Phase barrier/ separators between different phases are not installed. | Put purposely made phase separator (rubber type) between two phases; also terminate cables by proper sized cable lugs and cover cable lugs by heat shrink. | Corrected | Apr 30 2015 | On 02/09/2015: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 16 | Lightning Protection System's (LPS) earth pit and electrical system's earth pits are interconnected. | Ensure separate earth pit for Lightning Protection System and electrical system. | Corrected | Jul 23 2015 | On 02/09/2015: Corrected. | 16 WEEKS | Corrected
Follow Up Inspection |  | 17 | New Finding: Transformer/ Generator body earthing cable is inadequate. | Use 10-12 mm dia bare copper conductor for reliability; or the earth cable size must not be less than half of the phase cable (LT cables). | Corrected | Dec 14 2015 | On 07/02/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 18 | New Finding: Transformer Arcing horns are not installed. | Install transformer arcing horn with proper alignment (maintain not less than 2 inch gap between two horns.) | Corrected | Oct 14 2015 | On 07/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 19 | New Finding: Leakage current collector is not earthed. | Connect leakage current collector (armour) to earth. | Corrected | Oct 14 2015 | On 07/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Battery cases are kept on non-combustible materials. | Use non-flammable case/shelf to store battery. | Corrected | Oct 14 2015 | On 07/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 21 | New Finding: Circuit breakers are not adjusted accordingly. | Adjust all the CBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Corrected | Dec 31 2016 | On 07/02/2016: This issue is not done yet. New committed timeline is given till 31-3-16 to close the issue. On 13/04/2016: Not corrected. New time line is given till 30/05/2016. On 02/08/2016: Not corrected. On 13/10/2016: Not corrected. On 12/12/2016: Not corrected. On 27/03/2017: Not corrected. On 07/06/2017: Not corrected. On 18/12/2017: Not corrected. On 02/07/2018: Not corrected. On 21/11/2018: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Sub station room has inadequate ventilation. | Ensure/Arrange cross ventilation sub station room; You may use fire damper if you have to keep any opening on the corridors/egress path/exit. | Corrected | Jan 14 2016 | On 07/02/2016: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Cables are hanging without support and laid on floor. | Provide support to cables by using ladder type cable tray or by any suitable means. Do not make any arrangement that obstacle personnel's movement within working clearance. | Corrected | Nov 14 2015 | On 07/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 24 | New Finding: No/Inadequate rubber (insulation) mat on the working are of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries). | Corrected | Oct 14 2015 | On 07/02/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 25 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory and finally factory may share the SLD with the Accord for a review. | Corrected | May 30 2016 | On 07/02/2016: This issue is not done yet. New committed timeline is given till 31-3-16 to close the issue. On 13/04/2016: SLD has been submitted to ACCORD for review. New time line is given till 30/05/2016. On 02/08/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 26 | New Finding: Earth Pit resistance record is maintained poorly. Again, Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. Again, all earthing systems shall be tested for resistance on any dry day not less than once in every two years and records should be preserved. | Corrected | Feb 29 2016 | On 13/04/2016: Corrected. On 07/02/2016: Earth pit resistance record is OK but still the earth pits are not identifiable. New committed timeline is given till 29-2-16 to close the issue. | 2 Months | Corrected
Follow Up Inspection |  | 27 | New Finding: Lightning Protection System(LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Corrected | Jun 15 2016 | On 24/07/16: Not corrected. Down conductor is covered by PVC conduit and main conductor is under sized. Factory committed timeline: 20/08/16. On 15/05/2017: Not corrected. On 13/09/2017: Not corrected. On 14/02/2018: Not corrected. i).Design is not as-built. ii).No earth pit resistance test was conducted. iii).Clamps for two conductors are improperly installed iv).One earth pit was inaccessible. v).One air terminal was inadequate in size. vi).Base plates are not properly installed on 2 staircase-roofs. On 02/07/2018: Installation was found on going but not completed. On 21/11/2018: Not corrected. On 09/09/2019: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 28 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Corrected | May 30 2016 | On 02/08/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 29 | New Finding: Multiple cables terminated at MCCB terminals/ Bus bar. | Terminate each power cable at single terminal and use proper sized cable lug. | Corrected | May 30 2016 | On 02/08/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Flexible PVC pipe has been used inside the panel to cover cables. | Remove all the flexible PVC pipes from inside of the panel. | Corrected | May 30 2016 | On 02/08/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 31 | New Finding: Hot spots at terminations inside panel. | Identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such points. | Corrected | Dec 31 2016 | On 12/12/2016: Not corrected. On 27/03/2017: Not corrected. On 07/06/2017: Not corrected. On 18/12/2017: Not corrected. On 02/07/2018: Not corrected On 21/11/2018: Not corrected. On 09/09/2019: Corrected. No major hotspot found during inspection. | Immediate | Corrected
Follow Up Inspection |  | 32 | New Finding: Instruction for CPR Cardiopulmonary Resuscitation or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installation (LT panel, MDB, FDB, DB, SDB) at visible location. | Corrected | Dec 1 2017 | On 27/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Factory does not have any PPE and electrical tools. | Arrange PPE and electrical tools to use during electrical installation, repair and maintenance. | Corrected | Dec 1 2017 | On 27/03/2017: Not corrected. New Committed timeline is given till 30/04/2017. On 07/06/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 34 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personnel and workers will be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Corrected | Apr 30 2017 | On 07/06/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 35 | New Finding: Cables inside distribution board are disorganized. | Cables inside each distribution board shall be well organized to avoid misleading during any troubleshooting, distribution board form is appreciated. | Corrected | Apr 30 2017 | On 07/06/2017: Not corrected. On 18/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Excessive lint and dust inside the cable trench. | Conduct regular maintenance program to keep the cable trench clean. | Corrected | Apr 30 2017 | On 07/06/2017: Not corrected. Magnetic ballast found inside the cable channel/duct. On 18/12/2017: Not corrected. On 02/07/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 37 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Corrected | Jan 30 2018 | On 18/12/2017: Not corrected. New committed time line is given till 30/01/2018. On 02/07/2018: Not corrected. On 21/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Maintenance record doesn't reflect with housekeeping. | Periodic maintenance must be done in the facility; proper and relevant documentation shall be kept. | Corrected | Jul 15 2017 | On 18/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Corrected | Jul 15 2017 | On 18/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: 1. Distribution boards have no clear identification markings. 2. List of circuit or SLD of existing circuits are not available on each electrical panel/ board. | 1. All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. 2. List of circuit or SLD of respective circuits shall be available for each electrical panel/board. | Corrected | Jul 15 2017 | On 18/12/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 41 | New Finding: Electrical power cables are not identified properly. | Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | done | Jan 30 2018 | On 18/12/2017: Not corrected. New committed time line is given till 30/01/2018. On 02/07/2018: Not corrected. On 21/11/2018: Not corrected. On 09/09/2019: Not corrected. On 20/10/2020: Not done as per requirement. Not corrected. On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: At cutting section power sockets were found hanging. | Power socket has to be installed with proper rocking arrangement for cables. Need to provide rigid support/base and at minimum 200mm above floor level. It cannot be hanged. | Corrected | Aug 25 2018 | On 21/11/2018: Corrected. No such issue was found during inspection. | 1.5 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. Electrical SLD must be updated properly when electrical system is modified. | Work Completed | Oct 20 2019 | On 20/10/2020: Factory personnel submitted SLD to RSC for review purpose. Not corrected. On 01/10/2023: Not corrected. Some progress has been observed. Factory shall follow all the comments given on accepted SLD and make as built. Individual protection found missing in some places. On 04/03/2024: Not corrected. Few mismatches (Oversized breaker, Cable information mismatch, Load identification missing, and Inadequate Generator ECC) were found during inspection. 70% progress has been observed. On 20/07/2025: Not corrected. Almost 80% progress has been observed. However, there are some mismatches between the accepted SLD and the actual installation, including load/circuit identification, oversized/missing CB, cable information and missing individual protection. ON 06/10/2025: RPO Comments: Factory informed that the work is completed from their end. so it will be verified during next follow up inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 44 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | done | Oct 20 2019 | On 20/10/2020: Not done in all locations. Not corrected. On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | done | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. |  | Dec 10 2020 | On 01/10/2023: Not corrected. Test result found not satisfactory. On 04/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Earth Pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | done | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Insulation resistance test of electrical cables is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off) . | done | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Thermo graphic scanning of the entire electrical system has not been tested and recorded. | Thermo graphic scanning for the entire electrical system must be performed on a bi-annual basis and recorded. Find the cause of excessive heat-rise which may be the overloading, loose connection, unbalanced load and others and and take action accordingly. | done | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: List of circuit or SLD of existing circuits are not available in each electrical panel board. | List of circuit or SLD of existing circuits shall be available for each electrical panel board. | We have changed our circuits according to approved SLD. | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Cable conduit is wrapped by rived Flexible PVC cover. Power Cables are hanging without proper support. | Remove this sort of wrapping materials and clean the conduit properly. Seal the cover ( if it is wooden conduit replace it by nonflammable material). Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | done | Dec 10 2020 | On 01/10/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate space around transformer for performing maintenance work. | Ensure minimum 1.07m working space around the transformer (and related electrical installations). | Work completed as per accepted drawing. | Dec 10 2020 | On 01/10/2023: Not corrected. Minimum working space (1.07m) has not found around the transformer. On 04/03/2024: Not corrected. Factory has worked on this issue but still found inadequate clearance in one corner for a structural column. Factory has prepared a layout and sent it to RSC for review.Uneven height of cable trench in the transformer room has also been observed. The workplace around the transformer shall be at the same height. On 20/07/2025: Not corrected. No significant progress has been observed since the last follow-up. ON 21-DEC-2025: RPO Comments: issue will be verified during next follow up inspection | 1 Month | Pending Verification
Follow Up Inspection |  | 53 | New Finding: Transformer Oil Test report is not prepared as per requirement. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. We appreciate your report done by Govt. Authority. | done | Dec 10 2020 | On 01/10/2023: Corrected. The test report is prepared as per requirement. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: No policies for PPE & LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of the personnel during any kind of maintenance work. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO register. | Corrected | Nov 9 2023 | On 04/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Non rated and non-certified comb bar used for powering multiple MCB. | For connecting multiple MCB use rated and listed comb bar. | Corrected | Dec 17 2023 | On 04/03/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 56 | New Finding: Hot spots have been observed at some points. (above 40ºC of ambient). | Hot spots must be eliminated from entire electrical system. | Work Completed | Apr 6 2024 | On 20/07/2025: Not corrected. Significant progress has been observed, but hot spots are still found on some panels. ON 06/10/2025: RPO Comments: Factory informed that the work is completed from their end. so it will be verified during next follow up inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 57 | New Finding: Lightning Protection System (LPS) is not installed properly, including improper air terminal spacing, two-way connection missing etc. | Factory required to be redesign the Lightning Protection System (LPS) as per standard for the entire facility. Once the LPS is properly designed, it must be installed according to the design specifications to ensure effective protection against lightning strikes. | Work Completed | Oct 20 2025 | ON 06/10/2025: RPO Comments: Factory informed that the work is completed from their end. so it will be verified during next follow up inspection. | 3 Months | Pending Verification
Follow Up Inspection |  | 58 | New Finding: No policies for PPE/LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement PPE (Personal Protective Equipment) and LOTO (Lock-Out-Tag-Out) policy using LOTO devices to ensure personnel safety during maintenance activities. All LOTO usage records must be maintained for compliance and safety monitoring. | Work Completed | Aug 20 2025 | ON 06/10/2025: RPO Comments: Factory informed that the work is completed from their end. so it will be verified during next follow up inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 59 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. | Work Completed | Aug 20 2025 | ON 06/10/2025: RPO Comments: Factory informed that the work is completed from their end. so it will be verified during next follow up inspection. | 1 Month | Pending Verification

## Boiler
Date
15-Mar-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Mahadi Fashion (Pvt.) Ltd., Basugaon, Pubail, Gazipur Sadar, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2022-06-27
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 9293 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 8707 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near the entrance door. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9293 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. The marking and writing should be done on a separate arrangement, not on the gauge glass. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 8707 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. The marking and writing should be done on a separate arrangement, not on the gauge glass. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 8707 | Necessary technical documents (Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation and water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. Only electrical wiring diagram picture is attached and mentioned by the factory. Please arrange all other documents according to action plan. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 9293 | Necessary technical documents (Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories & feed water pump, operation and maintenance manual, water treatment design & calculation and water treatment report) were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. Only electrical wiring diagram picture is attached and mentioned by the factory. Please arrange all other documents according to action plan. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 9293 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Completed | Apr 21 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 8707 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | Completed | Apr 21 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 9293 | Fuel gas line safety valve(s) /pressure relief valve(s) blowoff is not directed to the outside of the boiler room. | Any fuel gas line safety valve or pressure relief valve blowoff shall be diverted to the outside of the boiler room (open to atmosphere condition) to prevent gas accumulation in the boiler room. | Completed | Apr 21 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 8707 | Fuel gas line safety valve(s) /pressure relief valve(s) blowoff is not directed to the outside of the boiler room. | Any fuel gas line safety valve or pressure relief valve blowoff shall be diverted to the outside of the boiler room (open to atmosphere condition) to prevent gas accumulation in the boiler room. | Completed | Apr 21 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 9293 | Nameplates for feed pump and safety valve were illegible / covered with paint and scratches. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 8707 | Nameplates for feed pump and safety valve were illegible / covered with paint and scratches. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer's technical documents regarding the equipment shall be provided. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 9293 | A boiler with a height of 8 feet or more was observed with an inadequate platform and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet and a railing with a minimum height of 3.5 feet should be provided. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 8707 | A boiler with a height of 8 feet or more was observed with an inadequate platform and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet and a railing with a minimum height of 3.5 feet should be provided. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 9293 | Water leakage/Spilled water was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 8707 | Water leakage/Spilled water was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 9293 | Visual flame monitoring glass was broken/out of order. | The visual flame monitoring glass shall be replaced with an appropriate one. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 18 | BB 9293 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 19 | BB 8707 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 9293 | Fuel line was not constructed with appropriate materials and was not properly supported and protected against corrosion. | Fuel line shall be constructed with appropriate materials as specified by the manufacturer/standard. Support and protection against corrosion shall be as per the requirements of the gas supply company and NFPA 54. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 8707 | Fuel line is not constructed with appropriate materials and is not properly supported and protected against corrosion. | Fuel line shall be constructed with appropriate materials as specified by the manufacturer/standard. Support and protection against corrosion shall be as per the requirements of the gas supply company and NFPA 54. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 9293 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 8707 | Installed pressure gauge was inadequate in dial size and pressure rating according to manufacturing standard. | An appropriate pressure gauge according to Bangladesh boiler regulation (BBR)/manufacturing standard/any standard recognized by the CIoB. shall be provided. | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 24 | BB 9293 | There was no visual flame monitoring system in place. | A visual flame monitoring system is required to be installed. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 25 | BB 9293 | The control panel cabinet does not specify the names of all boiler interlock alarm functions. | Names of boiler interlock alarm functions should be specified on the cabinet. | Completed | Jul 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 3 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 26 | BB 9293 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 27 | BB 8707 | There is no drainage available for water level gauge glass | A suitable discharge pipe shall be fitted with each water gauge drain cock or valve | Completed | Jun 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 28 | BB 9293 | Salt and scale formation was observed on the waterside inside the boiler about 2-3 mm (soft scale). | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 29 | BB 8707 | One of the available safety valves were not functioning. | The non-functioning safety valve(s) must be repaired or replaced if necessary. | Completed | Apr 21 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 30 | BB 8707 | Salt and scale formation was observed on the waterside inside the boiler about 1-2 mm (soft scale). | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 31 | BB 8707 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 32 | BB 8707 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 33 | BB 9293 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 34 | BB 9293 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | Completed | May 7 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 35 | BB 9293 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | Completed | Apr 13 2025 | Comments on 08-May-2025: The remediation work will be verified during the next follow-up inspection. | 1 WEEKS | Pending Verification