## Structural
Date
26-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd, Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2019-07-25
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Faulty connection. | Building engineer is required to investigate the connections and prepare an adequacy report with proper remedial actions. | Corrected | Dec 15 2019 | On 03-Mar-2020: This issue is required to cover under EA. During inspection EA has been prepared on site. But factory didn't submit EA to ACCORD till date of inspection. Factory is required to submit the EA to ACCORD. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. On 06-Jan-2022: Factory has produced revised EA report for main production building which was re-accepted from RSC on 06 November 2021. On 24-Aug-2022: Corrected from previous inspection. This issue has been covered in EA which has been re-accepted from RSC on 19th April 2022. On 15-May-2025: Corrected Previously. | 6 Weeks | Corrected
Initial Inspection |  | 2 | Faulty connection. | Carry out any remedial actions as per the adequacy report. | Corrected | Apr 30 2020 | On 03-Mar-2020: This issue is required to cover under EA. Factory is required to submit the EA to ACCORD. Also factory is required to carry out all remedial works arise from EA. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. Some faulty connections were observed during verification inspection. Factory authority is required to carry out remedial works as per the recommendation of the accepted EA. On 06-Jan-2022: Factory has produced revised EA report for main production building which was re-accepted from RSC on 06 November 2021. As per EA recommendation, factory has completed retrofitting work (installing vertical bracing). But during inspection, still faulty connection(missing bolt) was found in several location. Factory is required to install bolts as per connection details. On 24-Aug-2022: Factory had completed all remediation work as per previously accepted retrofitting drawing. Additionally, factory had repaired all connection gaps and installed missing bolts. However, as per re-accepted EA no additional remediation work is required. On 15-May-2025: Corrected Previously. Remediation completed. | 6 Months | Corrected
Initial Inspection |  | 3 | Discrepancies in drawings. | Building Engineer is required to survey the as-built structure and update the as-built drawings. | Corrected | Nov 17 2019 | On 03-Mar-2020: As-built drawing is required to produced as a part of EA. Factory is required to submit EA to ACCORD. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. On 06-Jan-2022: A set of as built drawing has been produced and re accepted by RSC on 06 November 2021. During inspection, 2nos vertical bracing was found sifted to another grid (A/9,10 and D/7,8) which is not as per drawing. Factory engineer is required to re-install the shifted bracing as per accepted drawing or revise the as-built drawing and check whether the existing bracing system is adequate or not. On 24-Aug-2022: As-built drawing has been produced as a part of EA which has been re-accepted from RSC on 19th April 2022. During inspection as-built drawing was found satisfactory with as-built condition. On 15-May-2025: Corrected Previously. | 6 Weeks | Corrected
Initial Inspection |  | 4 | Discrepancies in drawings. | Based on the as-built drawings review the design. | Corrected | Nov 24 2019 | On 03-Mar-2020: As-built drawing is required to produced as a part of EA. Factory is required to submit EA to ACCORD. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. On 06-Jan-2022: A set of as built drawing has been produced and re accepted by RSC on 06 November 2021. During inspection, 2nos vertical bracing was found sifted to another grid (A/9,10 and D/7,8) which is not as per drawing. Factory engineer is required to re-install the shifted bracing as per accepted drawing or revise the as-built drawing and check whether the existing bracing system is adequate or not. On 24-Aug-2022: This issue has been covered in EA which has been re-accepted from RSC on 19th April 2022. On 15-May-2025: Corrected Previously. | 6 Weeks | Corrected
Initial Inspection |  | 5 | Discrepancies in drawings. | Carry out remedial works if necessary. | Corrected | Dec 31 2019 | On 03-Mar-2020: As-built drawing is required to produced as a part of EA. Factory is required to submit EA to ACCORD. Also factory is required to carry out all remedial works arise from EA. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. Factory authority is required to carry out remedial works(if required) as per the recommendation of the accepted EA. On 06-Jan-2022: A set of as built drawing has been produced and re accepted by RSC on 06 November 2021. During inspection, 2nos vertical bracing was found sifted to another grid (A/9,10 and D/7,8) which is not as per drawing. Factory engineer is required to re-install the shifted bracing as per accepted drawing or revise the as-built drawing and check whether the existing bracing system is adequate or not. On 24-Aug-2022: Factory had completed all remediation work as per previously accepted retrofitting drawing. However, as per re-accepted EA no additional remediation work is required. On 15-May-2025: Corrected Previously. Remediation completed. | 6 Months | Corrected
Initial Inspection |  | 6 | Damage in beam, column & bracing. | Building engineer is required to take remedial action for the damage elements. | Corrected | Dec 15 2019 | On 03-Mar-2020: This issue is required to cover under EA. Factory is required to submit the EA to ACCORD. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. Damages were observed in beams and columns during verification inspection, Factory authority is required to carry out remedial works as per the recommendation of the accepted EA. On 06-Jan-2022: Factory has repaired damaged beam and column. During inspection, no damaged beams and columns were found. On 24-Aug-2022: Corrected from previous inspection. Factory had repaired all damaged members. On 15-May-2025: Corrected Previously. | 6 Weeks | Corrected
Initial Inspection |  | 7 | Proposed retrofit strengthening not implemented. | Building engineer is required to review the retrofitting scheme. | Corrected | Nov 30 2019 | On 03-Mar-2020: This issue is required to cover under EA. Factory is required to submit the EA to ACCORD. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. On 06-Jan-2022: Factory has produced revised EA report for main production building which was re-accepted from RSC on 06 November 2021. On 24-Aug-2022: Corrected from previous inspection. This issue has been covered in EA which has been re-accepted from RSC on 19th April 2022. On 15-May-2025: Corrected Previously. | 6 Weeks | Corrected
Initial Inspection |  | 8 | Proposed retrofit strengthening not implemented. | Carry out all the required remedial works as per the reviewed remedial drawings. | Corrected | Dec 31 2019 | On 03-Mar-2020: This issue is required to cover under EA. Factory is required to submit the EA to ACCORD. Also factory is required to carry out all remedial works arise from EA. On 07 -September 2021: This issue is required to be covered under EA. EA of the factory for the main production shed was accepted by RSC on 25 June 2021. During verification inspection, some mismatches were found between on-site and as built condition .According to the verification report, factory is required to submit the revised EA to RSC within 15 days of receiving this report. Factory authority is required to carry out remedial works ( if required) as per the recommendation of the accepted EA. On 06-Jan-2022: Factory has produced revised EA report for main production building which was re-accepted from RSC on 06 November 2021. As per EA recommendation factory has completed retrofitting work (Installation of vertical bracing). On 24-Aug-2022: Corrected from previous inspection. Factory had completed all remediation work as per previously accepted retrofitting drawing. However, as per re-accepted EA no additional remediation work is required. On 15-May-2025: Corrected Previously. | 6 Months | Corrected
Follow Up Inspection |  | 9 | New finding 01: Crack on brick wall found at admin building. | Factory enginner is required to investigate the extent of crack provide proper remeidal measure. | Corrected | Feb 22 2022 | On 06-Jan-2022: During inspection, cracks were found on brick wall at admin building of 1st and ground floor. Factory engineer is required to investigate the extent of crack provide proper remedial measure. On 24-Aug-2022: Factory has repaired all cracked areas as per investigation report. On 15-May-2025: Corrected Previously. Crack was not observed. | (within 6 weeks) | Corrected

## Fire
Date
26-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd, Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2019-07-25
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stair enclosures are separated from work areas and other spaces on each floor by fire-rated construction. Fire Doors have been provided with proper hour rating. But doors are kept open and installation of magnetic hold open device to interface with Fire Alarm System have been done but the devices are not interfaced with any approved FACP. Moreover Exit stair enclosures have unprotected openings within 10 feet towards production floor at two stairs. | The exit stair enclosure shall be provided with a minimum 1hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 0.75 hr. fire rated door and seal all penetrations and penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories. Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly shall be approved and/or designed by a qualified fire protection engineer. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | The issue fully remediated.as per the rsc recommendation. | Jan 30 2020 | On 30-Apr-2024: In progress. The exit stair enclosures are not separated from work areas and other spaces on 1st and 2nd floor (Male dining) at RCC building by fire-rated construction. Few Fire Doors have been provided with proper hour rating but doors are kept open by external object (i.e.: rope, cable, etc.). On 26-Nov-25: Progress has been observed. The factory has installed fire-rated doors to separate the exit stair enclosures on the 1st and 2nd floors of the RCC Admin Building and the doors were found interfaced with the fire alarm system. However, the gap beneath the fire doors was found greater than 19 mm. Additionally, unsealed gap was observed around the vision glass panel, as the glazing materials required to properly secure the vision glass to the door leaf were not provided. RPO Comments: On 05-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Initial Inspection |  | 2 | Exit stair(s) is discharge the occupants inside the building. | 1. Modify stair to discharge directly outside. Or 2. Provide 2-hr fire-rated exit passageway leading directly outside (vestibules to separate any storage areas). Or 3. Provide sprinkler protection for discharge floor in accordance with NFPA 13. | We have modified stair to discharge directly outside as per the RSC recommendation. | Jan 30 2020 | On 30-Apr-2024: In progress. 1st & 2nd floor (Female and Male dinning) exit stair is discharging the occupant inside the building. On 26-Nov-25: Corrected. The factory has provided an additional exit and reconfigured the existing exit discharge which leads directly to the exterior of the building. | Within 3 months | Corrected
Initial Inspection |  | 3 | The exterior exit stair is not separated from the building. | Exterior exit stairs shall be separated from the building with a rating requirement of 1 hr. fire rating for 3 or fewer stories or 2 hr. fire rating for 4 or more stories. The rating of the exterior wall shall extend 3.05 m (10ft) beyond the ends of the stair structure. | Work is progress,(It is completed 45% and rest of work will complete as soon as possible | Jan 30 2020 | On 30-Apr-2024: In progress. Exterior stair have unprotected openings and electrical appliance within 10 feet. On 26-Nov-25: Progress has been observed. The factory has relocated the electrical appliances that were within 10 feet of the exterior exit stair and has sealed the unprotected openings. However, a few unprotected openings still remain unsealed within 10 feet of the exterior exit stair. RPO Comments on 05-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 4 | Rooms used for combustible storage are not separated by fire rated construction. Location: Wastage go down shed at ground floor adjacent to the main building | Separate the dedicated storage rooms by minimum 1-hr fire rated construction. Provide 0.75 hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction. | We have completed Fire rated construction work by 10 inch Bricks wall as par the RSC recommendation. | Jan 30 2020 | On 30-Apr-2024: In progress. Rooms used for combustible storage are not separated by fire rated construction. Location: wastage go down shed at ground floor at North side, 1st floor at RCC building. On 26-Nov-25: Corrected. Storage was not found on the 1st floor of the RCC building during the inspection. Additionally, wastage godown shed at ground floor (North side) was found separated from the adjacent main building. | Within 3 months | Corrected
Initial Inspection |  | 5 | The existing fire alarm & detection system is not installed properly. Still few areas are out of detection system. | Submit the as-built design/drawing of fire alarm & detection system to Accord for review. | Work is progress,(It is completed 70% and rest of work will complete as soon as possible | Apr 30 2020 | On 30-Apr-2024: In progress. Fire alarm and detection system installation work almost completed. Reportedly. factory will submit the design to RSC for review. On 26-Nov-25: The initial FADS design (combining both ID: 23699 and ID: 24732 buildings) was reviewed by the RSC on 10 March 2025. The factory informed that the FADS installation & modification works are ongoing as per the reviewed design and will apply for Pre-T&CVI after completing all installation & required modification works within 3 weeks. However, during the inspection, the FACP was found active with several fault and trouble signal. RPO Comments: On 05-Feb-2026 the design documents have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | Within 06 Months (Design review & Modification of the system) | In Progress
Initial Inspection |  | 6 | Storage was located in the exit stair. | Remove all storage from exit stairs. | We have already removed all the storage from exit stairs location. > Completed. | Nov 7 2019 | On 30-Apr-2024: Corrected. On 26-Nov-25: Corrected. | Immediately | Corrected
Initial Inspection |  | 7 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | The issue fully remediated | Dec 31 2019 | On 30-Apr-2024: In progress. Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes at Ground floor in Shed. On 26-Nov-25: Corrected. Adequate illumination levels were observed along egress routes during the inspection. | Within 3 months | Corrected
Initial Inspection |  | 8 | Manual on-off switch is provided for emergency lighting / exit signage units. | Remove manual on/off switches from emergency lighting /exit signage units to prevent them from being switched off. | All manual on/off switch has been removed from emergency lighting /exit signage. > Completed. | Nov 20 2019 | On 30-Apr-2024: Corrected. On 26-Nov-25: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 9 | Dead-end aisles exceed 30 meter. Location: Mezzanine floor-office area. | Reconfigure the egress arrangement to reduce the maximum dead-end distance to not more than 30 meter. | Work is going on regarding this issue. > We are working on this issue. Hopefully it will be done by . 28.02.2022. Work is going on. Already Done | Jan 30 2020 | On 30-Apr-2024: Corrected. Additional exit provided. On 26-Nov-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire alarm system is not in accordance with NFPA 72 or as per Accord standard. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72 or as per Accord standard. | Work is progress,(It is completed 70% and rest of work will complete as soon as possible | Jul 31 2020 | On 30-Apr-2024: It is an integrated part of Fire Alarm System On 26-Nov-25: It is an integrated part of Fire Alarm & Detection System. RPO Comments: On 05-Feb-2026 the design documents have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | Within 3 month (After completion of the installation) | In Progress
Initial Inspection |  | 11 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with The ACCORD standard. Keep written records on-site. | The issue fully remediated | Jan 30 2020 | On 30-Apr-2024: In progress. Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with The RSC standard. On 26-Nov-25: Corrected. Inspection, testing, and maintenance record for the exit sign and emergency lighting system was provided during the inspection and maintained as per recommendation. | Within 3 months | Corrected
Initial Inspection |  | 12 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records on- site, in accordance with NFPA 10 and ACCORD standards. | > Completed. | Jan 30 2020 | On 30-Apr-2024: Corrected. On 26-Nov-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 13 | Building did not have stair designation signs and occupant load signs at required locations. | Provide stair designation signs and occupant load signs at required locations. | The issue fully remediated | Nov 5 2019 | On 30-Apr-2024: In progress. Building did not have stair designation signs and occupant load signs at required locations. On 26-Nov-25: Corrected. Provided as per recommendations. | Within 1 week | Corrected
Follow Up Inspection |  | 14 | New Finding(1st FUI): Evacuation map was not updated as per site condition. | Provide evacuation map as per site condition. | The issue fully remediated.as per the rsc recommendation. | May 30 2024 | On 30-Apr-2024: New Finding. On 26-Nov-25: The issue remains the same as before. RPO Comments: On 05-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Follow Up Inspection |  | 15 | New Finding(1st FUI): Headroom found less than 80inch at 1st floor Female dining exit and Storage room. | All means of egress shall have a minimum ceiling height of 2.3 m (7 ft 6 in.) with projections from the ceiling not less than 2.03 m (6 ft 8 in.). The minimum ceiling height shall be maintained for at least 2/3 of the space or room as long as the remaining area shall be not less than 2.03 m (6 ft 8 in.). Headroom on stairs shall not be less than 2.03 m (6 ft 8 in.). | The issue fully remediated.as per the rsc recommendation. | May 30 2024 | On 30-Apr-2024: New Finding. On 26-Nov-25: The factory has readjusted the headroom; however, the headroom was still found less than 80 inches (measured at 70 inches). RPO Comments: On 05-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Follow Up Inspection |  | 16 | New Finding (1st FUI): Exit discharge path from Ground floor's(Sewing section) Gate-4 are not separated from Electrical pump by fire rated construction. Location: East Side of Shed. | An egress court serving as a portion of the exit discharge shall be open to the sky or provided with a fire resistance rated enclosure the same as the exit enclosure. Egress courts less than 3050 mm (10 ft) in width (as measured from the building and the adjacent property line) shall be provided with walls having a 1-hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. Or, Remove electrical pump from Exit discharge path. | The issue is fully remediated | May 30 2024 | On 30-Apr-2024: New Finding. On 26-Nov-25: Corrected. The factory has removed the electrical pump from the exit discharge path. | Within 1 Month | Corrected
Follow Up Inspection |  | 17 | New Finding (2nd FUI): Exit sign not provided at exit. Location: Several Exit of Admin Building. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11. | The issue fully remediated.as per the rsc recommendation. | Dec 26 2025 | On 26-Nov-25: New Finding. RPO Comments: On 05-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 Month | Pending Verification
Follow Up Inspection |  | 18 | New Finding (2nd FUI): Transformer/sub-station room was not properly separated by fire rated construction with other occupancies/areas due to unsealed cable tray penetrations. Location: Ground floor of production shed. | Transformer room shall be separated from other occupancies by a minimum 2-hr fire rated construction (wall, floor, slab etc.). Switch gears and transformer bays shall be separately housed with a 2-hr rated wall in between. Seal all penetrations and openings by a minimum 1.5-hr fire rated materials to maintain the required fire separation. All exhaust systems shall discharge to the exterior of the building in a safe location. Oil filled transformers shall not be housed above ground level. Or, Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. | In progress | Feb 26 2026 | On 26-Nov-25: New Finding. RPO Comments on 05-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 Months | In Progress

## Electrical
Date
26-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd, Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2019-07-25
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by Accord. Electrical SLD must be updated properly when electrical system is modified. |  | Dec 30 2019 | On 28/Nov/2023: Not Corrected. Factory got accepted SLD from RSC on 13-Jun-2022. Few mismatches( Inadequate Generator body earth pit, ECC mismatch, Load identification mismatch, Individual protection missing/oversize, Busbar information mismatch, Inadequate ECC bar etc ) found from accepted sld. On 23/05/2024: Not corrected. Factory built an as-built SLD. Lots of changes found between accepted SLD & as-built installation. Several cables & breakers changed. Also 160A floor BBT is replaced by a 400A BBT. Factory needs to submit their SLD to RSC for review. RPO Comments: On 19-Aug-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 25/02/2026: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 2 | LPS main conductors are not securely connected with lug. | Conductors must be securely connected with lugs and terminated properly. Periodical maintenance with checklist is necessary. | This Issue is Fully Remediated. | Dec 30 2019 | On 28/Nov/2023: Not Corrected. LPS is not installed properly(Cross run conductor missing, Bi-metallic joint missing etc). On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 3 | Insulation resistance test of electrical power cables is not performed properly. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTHS | Corrected
Initial Inspection |  | 4 | Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 5 | Power Cables are hanging without proper support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 6 | Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Remediation work is going on. Our Electrical engineering team working on this issue. We hope that we will be remediate this issue within the short time. | Nov 30 2019 | On 28/Nov/2023: Not Corrected. Found in few SDB's. On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 7 | Large exhaust fans are controlled directly by MCB . | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | This Issue is Fully Remediated. | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 8 | Electrical equipment (Light) not supported properly . | Every electrical equipment must be supported properly. | Remediation work is going on. Our Electrical engineering team working on this issue. We hope that we will be remediate this issue within the short time. | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 9 | MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. |  | Dec 30 2019 | On 28/Nov/2023: Not Corrected. Rectification work will be done as per accepted SLD. On 23/05/2024: Not corrected. Factory completed their installation work after getting acceptance from RSC. RPO Comments: On 19-Aug-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 25/02/2026: Not Corrected. Significant progress has been observed; however, a few MCBs/MCCBs are still found to be oversized. Additionally, some individual protection devices are also identified as oversized. | 2 MONTHS | In Progress
Initial Inspection |  | 10 | Hot Spots were observed at several point. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 11 | Sharp edge of cable tray cover is not protected which will result potential damage of insulation of the cables. | Wiring systems must be selected and erected at a safe route without and sharp edge which can result insulation damage and consequently short circuit. The edge of the cable tray cover and the tray shall be blunt. |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 12 | Outdoor Cable trays are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. |  | Nov 30 2019 | On 28/Nov/2023: Corrected. | 1 MONTH | Corrected
Follow Up Inspection |  | 13 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar /Tap of box(TOB). | Each electrical circuit must be terminated at single MCB/MCCB/Tap of box (TOB) terminals. | Corrected | Jan 13 2024 | On 23/05/2024: Corrected. | 1 Month | Corrected

## Boiler
Date
26-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd, Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2023-06-01
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 10180 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | The work has already been completed . | May 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 10305 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | The work has already been complete | May 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 10180 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The work has already been complete | May 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 10305 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The work has already been complete | May 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 10180 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Contact is underway with the manufacturing company and document will be collected soon | May 8 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 10305 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Contact is underway with the manufacturing company and document will be collected soon | May 8 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 10180 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 10305 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 10180 | Inconsistency was observed between the actual safety valve size and the CIoB or Manufacturer approved safety valve size. | Actual safety valve size and manufacturer or CIoB approved safety valve shall be consistent. Any inconsistency shall be approved in writing from the CIoB and a copy to be preserved on site. | Contact is underway with the manufacturing company and document will be collected soon | May 8 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 10180 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 10305 | Inconsistency was observed between the actual safety valve size and the CIoB or Manufacturer approved safety valve size. | Actual safety valve size and manufacturer or CIoB approved safety valve shall be consistent. Any inconsistency shall be approved in writing from the CIoB and a copy to be preserved on site. | Contact is underway with the manufacturing company and document will be collected soon | May 8 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 12 | BB 10180 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Provided picture is registration number plate. The factory needs to ensure manufacturer's nameplate. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 13 | BB 10305 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Provided picture is registration number plate. The factory needs to ensure manufacturer's nameplate. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 14 | BB 10180 | Carbon deposition was found in the (smoke tubes/furnace chamber). | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | The work has already been complete | May 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 15 | BB 10305 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 16 | BB 10180 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 17 | BB 10305 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 18 | BB 10180 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 19 | BB 10305 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | The work has already been complete | Mar 15 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 20 | BB 10180 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | The work has already been complete | Mar 15 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 21 | BB 10305 | There was no acoustic alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 22 | BB 10180 | There was no acoustic alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | The work has already been complete | Apr 8 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification