## Structural
Date
26-Apr-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd (Extension), Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2023-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Lack of information in Assessment Report (Extension Shed | The building engineer is required to update the Assessment Report including all adequacy checks as per 1.9.1 of BNBC. | Our recent assessment report has been successfully submitted and is currently under review by the RSC. | Jan 19 2024 | On 09-Jun-2024: This issue is required to be covered under Engineering Assessment (EA). As per the last review comments on 31-March-2024, the factory is required to submit the updated EA documents within 23-June-2024. On 15-May-2025: This issue is required to be covered in EA. Factory has sent the EA documents by mail to RSC on 6 May 2025 which is currently under review to receive the submission. RPO Comments: On 02-Feb-2026 the design documents are pending to be re-submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 2 | Lack of information in Assessment Report (Extension Shed) | Implement remediation work if required | Our recent assessment report has been successfully submitted and is currently under review by the RSC. | May 4 2024 | On 09-Jun-2024: This issue is required to be covered under Engineering Assessment (EA). As per the last review comments on 31-March-2024, the factory is required to submit the updated EA documents within 23-June-2024. Any remediation work raised from EA is required to be implemented after getting acceptance of EA. On 15-May-2025: Any remediation work raised from EA is required to be implemented after getting acceptance from RSC. RPO Comments: On 02-Feb-2026 the design documents are pending to be re-submitted to RSC. | within 6 months | In Progress
Initial Inspection |  | 3 | Lack of information in as-built drawing (Extension Shed) | The building engineer is required to update the as-built drawing. | Our recent assessment report has been successfully submitted and is currently under review by the RSC. | Jan 19 2024 | On 09-Jun-2024: A set of as-built drawings were prepared as part of EA report. However, the factory is required to update the as-built drawings as per the observations identified in the initial inspection report. Moreover, during inspection, some additional discrepancies were found, which will be addressed in the next review comments. On 15-May-2025: As-built drawing has been produced and this issue is required to be covered in EA. Factory has sent the EA documents by mail to RSC on 6 May 2025 which is currently under review to receive the submission. RPO Comments: On 02-Feb-2026 the design documents are pending to be re-submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 4 | Gap in connection of column to baseplate and corrosion on steel members (Extension Shed) | The building engineer is required to fill the gaps with a suitable method | Column to baseplate connection gap has been filled with a suitable methode as per the CAP. This issue is fully Remediated. | Jan 19 2024 | On 09-Jun-2024: During inspection, it was found that factory has filled the gaps in connection between column and baseplate. On 15-May-2025: Corrected previously. During inspection no connection gap was found. | within 6 weeks | Corrected
Initial Inspection |  | 5 | Gap in connection of column to baseplate and corrosion on steel members (Extension Shed) | Provide rust proof paint on steel members to prevent corrosion. | Rust proof paint has been Provided on steel members for prevent corrosion. This issue is fully Remediated. | Jan 19 2024 | On 09-Jun-2024: During inspection, it was found that factory has removed corrosion of steel sections and also applied anti-corrosive paints. On 15-May-2025: Corrected previously. Factory has provided rust proof paint on steel members. | within 6 weeks | Corrected
Initial Inspection |  | 6 | Non-structural elements found unbraced/not anchored (Extension Shed) | The building engineer is required to brace/anchor all nonstructural elements. | All nonstructural elements has been removed by anchor. This issue is fully Remediated. | Jan 19 2024 | On 09-Jun-2024: During inspection, it was found that factory has anchored all the non-structural elements of Extension Shed. On 15-May-2025: Corrected previously. During inspection non-structural elements were found anchored and braced. | within 6 weeks | Corrected
Initial Inspection |  | 7 | Lack of as-built drawing (Utility Building, Wastage Shed, Fire pump Room, Security Building) | The building engineer is required to produce the as-built drawing. | Our recent assessment report has been successfully submitted and is currently under review by the RSC. | Jan 19 2024 | On 09-Jun-2024: A set of as-built drawings were prepared for Utility Building, Wastage Shed, Fire Pump Room, and Security Building. As per the last review comments on 31-March-2024, the factory is required to submit the updated as-built drawings within 23-June-2024. During inspection, some discrepancies were found in the as-built drawings of Fire Pump Room, which will be highlighted in the next review comments. On 15-May-2025: As-built drawing has been produced. Factory has sent the documents by mail to RSC on 6 May 2025 which is currently under review to receive the submission. RPO Comments: On 02-Feb-2026 the design documents are pending to be re-submitted to RSC. | within 6 weeks | In Progress
Initial Inspection |  | 8 | Corrosion on steel members (Wastage Room) | Provide rust proof paint on steel members to prevent corrosion | Rust proof paint has been Provided on steel members for prevent corrosion. This issue is fully Remediated. | Jan 19 2024 | On 09-Jun-2024: During inspection, it was found that factory has removed corrosion of steel sections and applied anti-corrosive paints. On 15-May-2025: Corrected previously. During inspection no further corrosion was found. | within 6 weeks | Corrected
Follow Up Inspection |  | 9 | New Finding 1: Significant gaps found in the steel connections (Extension Shed) | The building engineer is required to fill the gaps with a suitable method. | Fully remediated | Jul 25 2024 | On 09-Jun-2024: During inspection, significant gaps were found at the connection of rafter-rafter joint of Extension Shed. The building engineer is required to fill the gaps in connections with a suitable method. On 15-May-2025: Factory has repaired/filled the connection gap. | within 6 weeks | Corrected
Follow Up Inspection |  | 10 | New Finding 2: Missing bolts found at the rafter end plate connection (Extension Shed) | Survey the whole structure and install the missing bolts. | Fully remediated | Jul 25 2024 | On 09-Jun-2024: During inspection, missing bolts were observed at the rafter end plate connection of Extension Shed. The building engineer is required to survey the whole structure and install the missing bolts in suitable method. On 15-May-2025: Factory has installed the missing bolts. | within 6 weeks | Corrected
Follow Up Inspection |  | 11 | New Finding 3: Loose roof and wall bracing found (Extension Shed) | Identify all the loose bracings and tighten accordingly. | This Issue ids Fully remediated | Jul 25 2024 | On 09-Jun-2024: During inspection, loose roof and wall cable bracings were found at the Extension Shed. The building engineer is required to identify all loose bracings and tighten accordingly. On 15-May-2025: The factory has removed all the cable bracing since those are not considered in EA. | within 6 weeks | Corrected

## Fire
Date
26-Apr-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd (Extension), Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2023-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Room used for combustible storage are not separated by fire rated construction. Location: Extension Shed. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | In progress | Mar 4 2024 | On 26-Nov-25: Remediation work has not been started yet. The issue remains the same as before. RPO Comments on 02-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 2 | Areas used for combustible storage are not separated by fire rated construction. Location: Extension Shed | Provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m | This is in-process materials. Regarding this issue we have maintained the miscellaneous requirements as per RSC guideline such as: - Maximum height of 2.4m and maximum area of 23m2 | Mar 4 2024 | On 26-Nov-25: Corrected. In-process storage were found within the recommended limit during the inspection. | Within 3 months | Corrected
Initial Inspection |  | 3 | Manual on-off switch is provided for emergency lighting / exit sign units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | This Issue is fully remediated | Jan 4 2024 | On 26-Nov-25: Corrected. Switches has been found non-functional during the inspection. | Within 1 month | Corrected
Initial Inspection |  | 4 | The directional signs are not provided where there is a change in direction and where the continuation of the egress path is not obvious. Location: Extension Shed. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | The issue is fully remediated. | Jan 4 2024 | On 26-Nov-25: Corrected. Provided as per recommendation. | Within 1 month | Corrected
Initial Inspection |  | 5 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Extension Shed. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | This Issue is fully remediated | Jan 4 2024 | On 26-Nov-25: Corrected. Adequate illumination levels were observed along egress routes during the inspection. | Within 1 month | Corrected
Initial Inspection |  | 6 | Exit signs were placed in areas that were not exits. | Remove exit signs (double sided) from noted areas to avoid confusion from actual exits. | Fully Remediated | Jan 4 2024 | On 26-Nov-25: Corrected. The factory has removed the exit sign from one side as per the recommendation. | Within 1 month | Corrected
Initial Inspection |  | 7 | Inspection, testing, and maintenance for the exit sign and emergency lighting system was not in accordance with RSC Technical Guidelines (Standard). | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with RSC Technical Guidelines (Standard). Keep written records on-site. | Completed | Jan 4 2024 | On 26-Nov-25: Corrected. Inspection, testing, and maintenance record for the exit sign and emergency lighting system was provided during the inspection and maintained as per recommendation. | Within 1 month | Corrected
Initial Inspection |  | 8 | The egress court (east exit discharge path) is found unprotected. | Seal all penetrations and openings along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. Alternatively, provide a second remote discharge path to the public way (only include this if feasible). | In progress | Mar 4 2024 | On 26-Nov-25: Remediation work has not been started yet. The issue remains the same as before. RPO Comments on 02-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 months | In Progress
Initial Inspection |  | 9 | Fire evacuation maps posted at the entrance of the exits were not updated. | Fire evacuation maps shall be posted at the entrance of each exits and maps shall be updated regularly when required. | This Issue is fully remediated.Evacuation maps have been provided according to the location | Jan 4 2024 | On 26-Nov-25: Remediation work has not been started yet. The issue remains the same as before. RPO Comments: On 02-Feb-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Initial Inspection |  | 10 | Occupant load signs at required exits are not posted in accordance with the RSC Technical Guidelines (StandardV1.0) section 6.4.4 | Provide occupant load signs at required locations. | Completed | Jan 4 2024 | On 26-Nov-25: Corrected. Provided as per recommendation. | Within 1 month | Corrected
Initial Inspection |  | 11 | Sliding doors are provided at building exits. | Replace all collapsible and sliding doors along the means of egress with side-hinged, swinging egress doors | In progress | Jan 4 2024 | On 26-Nov-25: Remediation work has not been started yet. The issue remains the same as before. RPO Comments on 02-Feb-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Initial Inspection |  | 12 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10. | Completed | Jan 4 2024 | On 26-Nov-25: Corrected. Inspection, testing, and maintenance record for the portable fire extinguisher was provided during the inspection and maintained as per recommendation. | Within 1 month | Corrected
Initial Inspection |  | 13 | The fire alarm system installation requires detailed review to confirm compliance with NFPA 72 and RSC technical guidelines (standard). | Submit as-built drawings, testing records, equipment certification and other relevant documentation to the RSC for review. Once reviewed, install or modify the fire detection and alarm system (where required) throughout the building in accordance with RSC technical guidelines (standard). and NFPA 72. The factory management shall contact RSC to conduct the final acceptance testing after the installation, testing & commissioning. | Work is progress,(It is completed 70% and rest of work will complete as soon as possible | Apr 4 2024 | On 26-Nov-25: The initial FADS design (combining both ID: 23699 and ID: 24732 buildings) was reviewed by the RSC on 10 March 2025. The factory informed that the FADS installation & modification works are ongoing as per the reviewed design and will apply for Pre-T&CVI after completing all installation & required modification works within 3 weeks. However, during the inspection, the FACP was found active with several fault and trouble signal. RPO Comments: On 02-Feb-2026 the design documents have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | Design- within 1 Month Modification if required- within 3 Months | In Progress
Initial Inspection |  | 14 | Inspection, testing and maintenance for the fire detection and alarm system was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with Table-14.3.1 of NFPA 72. | Work is progress,(It is completed 60% and rest of work will complete as soon as possible | May 4 2024 | On 26-Nov-25: It is an integrated part of Fire Alarm & Detection System. RPO Comments: On 02-Feb-2026 the design documents have been reviewed and accepted by RSC. The remediation needs to be competed based on accepted design. | 1 Month after installation. | In Progress

## Electrical
Date
26-Apr-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd (Extension), Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2023-11-09
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineers and getting it reviewed by RSC. Electrical SLD must be updated properly when the electrical system is modified. | The SLD has been approved by RSC on Tuesday, April 30, 2024 12:49 PM by email. | Mar 4 2024 | On 23/05/2024: Corrected. | 3 MONTHS | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not installed where the risk index equal or greater than 40 (According to BNBC) | Factory shall design Lightning Protection System (LPS) for the whole factory (where the Risk index is equal or greater than 40). Once LPS is designed properly, installation must be done accordingly. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 3 | No policies for PPE & LOTO (Lock-Out-Tag? Out) are introduced for safety of the personnel during any kind of the personnel during any kind of maintenance work. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 4 | There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 5 | Insulation resistance test of electrical power cables is not performed. | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 6 | Thermographic survey is not performed for whole panel board (partially done on circuit breaker) | Thermography survey shall be conducted on entire electrical system in the facility at least twice in a year. And the remediation suggestions mentioned in the report shall be carried out. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 7 | Earth Pit resistance test record doesn't match with field. | Adequate number of earth pits must be ensured (if it's lower in numbers) and record must be made accordingly. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 8 | Hot spots have been observed at some points. (above 40ºC of ambient) | Hot spots must be eliminated from the entire electrical system. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 9 | No working separation between LT ( Low Tension) panel/s and HT (High Tension) unit/s (Transformer, HT switchgear)] | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07m) and ventilation must be ensured. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 10 | Generator terminal box left open to allow cable entry.] | Base plate for generator terminal box must be installed and cables entering terminal box must be firmly fixed with cable gland. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 11 | Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 12 | Power cables are bent excessively | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 13 | Panel body is not connected to earth. Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 14 | Circuit breaker has no capacity information. | Each Circuit breaker must have its own capacity information. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 15 | Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 16 | Outdoor Cable are not covered to protect from weather effect. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 17 | Combustible material attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from combustible material and water pot. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 18 | Large exhaust fans are controlled directly by MCB. | Induction motor driven fans (which has high inrush current) must not be operated directly using MCB; Direct-On-Line (DoL) type control switch must be used. | This Issue is Fully Remediated. | Feb 4 2024 | On 23/05/2024: Corrected. | 2 MONTHS | Corrected
Initial Inspection |  | 19 | BBT plug point/ Feed box left open. | Unused BBT plug point/ Feed box must be sealed/covered by BBT plug cap/ gland or by insulating material. | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected
Initial Inspection |  | 20 | Electrical machines are operated without ensuring proper insulations. | All the electrical machines which are operated directly by the operators and have chances of electrical shock shall be ensured a safe work place around each of them. Insulated rubber mat shall be kept around each machine (especially on working spaces) | This Issue is Fully Remediated. | Jan 4 2024 | On 23/05/2024: Corrected. | 1 MONTH | Corrected

## Boiler
Date
26-Apr-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Nassa Spinners and Garments Ltd (Extension), Plot No.- 197-199, 200 (part), Comilla EPZ, Comilla, Comilla
Date of Inspection |  | 2023-06-01
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 10180 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | The work has already been completed . | May 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 10305 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | The work has already been complete | May 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 10180 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The work has already been complete | May 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 10305 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | The work has already been complete | May 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 10180 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Contact is underway with the manufacturing company and document will be collected soon | May 9 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 6 | BB 10305 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance logbook, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | Contact is underway with the manufacturing company and document will be collected soon | May 9 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 7 | BB 10180 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 8 | BB 10305 | Boiler Safety Valve outlet line was not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support and drainage system. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 10180 | Inconsistency was observed between the actual safety valve size and the CIoB or Manufacturer approved safety valve size. | Actual safety valve size and manufacturer or CIoB approved safety valve shall be consistent. Any inconsistency shall be approved in writing from the CIoB and a copy to be preserved on site. | Contact is underway with the manufacturing company and document will be collected soon | May 9 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 10 | BB 10180 | Boiler exhaust gas pipeline inside the boiler room was found with improper insulation. | Proper insulation to boiler exhaust gas pipeline inside the boiler room causing heat exposure for personnel shall be provided. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 10305 | Inconsistency was observed between the actual safety valve size and the CIoB or Manufacturer approved safety valve size. | Actual safety valve size and manufacturer or CIoB approved safety valve shall be consistent. Any inconsistency shall be approved in writing from the CIoB and a copy to be preserved on site. | Contact is underway with the manufacturing company and document will be collected soon | May 9 2026 | Comments on 26-Apr-2026: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 12 | BB 10180 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Provided picture is registration number plate. The factory needs to ensure manufacturer's nameplate. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 13 | BB 10305 | The boiler manufacturer's nameplate was not available on the boiler. | The boiler manufacturer's nameplate shall be available on the boiler with accurate technical information and boiler manufacturer's name in standard language. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. Provided picture is registration number plate. The factory needs to ensure manufacturer's nameplate. | 1 MONTH | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 14 | BB 10180 | Carbon deposition was found in the (smoke tubes/furnace chamber). | The furnace and inside of the fire tubes should be cleaned periodically to prevent excessive soot build-up. The fuel burner should be adjusted according to the manufacturer's guidelines. | The work has already been complete | May 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | Functional test inspection | 15 | BB 10305 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 16 | BB 10180 | The Air Pressure Limiter was missing. | Air Pressure Limiter shall be installed and kept functional. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: Based on the visual evidence provided, it remains unclear whether the issue has been fully resolved.. The remediation work shall be done following guidelines provided and applicable standard within the committed timeline. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 17 | BB 10305 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 18 | BB 10180 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 19 | BB 10305 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | The work has already been complete | Mar 16 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 20 | BB 10180 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | The work has already been complete | Mar 16 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 21 | BB 10305 | There was no acoustic alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 22 | BB 10180 | There was no acoustic alarm when the limiter was activated. | An acoustic with optical alarm should be installed. | The work has already been complete | Apr 9 2026 | Comments on 26-Apr-2026: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification