## Structural
Date
14-May-2026 |  | STRUCTURAL & BUILDING SAFETY
Bangladesh Accord Remediation Summary of Actions Required
Factory Name & Address |  | A.M.C.S. Textiles Limited, 41 & 52 AEPZ Narayangonj Bangladesh, Narayanganj, Dhaka
Date of Inspection by Accord |  | 2014-05-18
Accord Rating
Finance Plan Agreed
Item No | Accord Inspection Observation | Accord Action Plan | Final Action Plan | Final Timeline | Comments from Accord | Accord Timeline | Progress Status
1 | High storage loads | * Structural Engineer to check the connections capacities of all steel connections. * Repairs and alterations to be made to the steel connections as required and as advised by the Structural Engineer. | Facility management is communicating with the Structural Assessment providers to visit the factory and to complete the required actions as presribed by Accord. | 26/11/2014 |  | Within 6 weeks. | In Progress
2 | High storage loads | * Structural Engineer to assess the slack roof bracing and the missing diagonal bracing in the 3rd floor. * Repairs to be carried out as required. | Facility management is communicating with the Structural Assessment providers to visit the factory and to complete the required actions as presribed by Accord. | 26/11/2014 |  | Within 6 weeks. | In Progress
3 | High storage loads | * Structural Engineer to provide detailed calculations for the mezzanine floor. These should confirm structure’s ability to support storage loading and its extends. | AMCS has load assessment records on the ground floor's mezzanine structures. | 11/11/2014 |  | Within 6 weeks. | In Progress
4 | Inconsistencies with permit drawings | * Structural engineer to confirm loadbearing system at Ground Floor slab level. * Produce and actively manage a loading plan for all floor plates including ground floor and mezzanine floors within the factory giving consideration to floor capacity and column capacity. | AMCS has pre-construction soil test reports; and as discussed with the Accord 23.09.14 the lower ground floor can with held the whole building, and as agreed this NC's is not vaild. | 26/11/2014 |  | Within 6 weeks. | In Progress
5 | Inconsistencies with permit drawings | * The Building Engineer to check that the as-built structure (no central column row in 3rd floor and steel structure for office blocks in 2nd and 3rd floor) is in alignment with the structural design. * Carry out any structural alterations as advised by the Structural engineer. | Misinterpretation regarding the structural drawings as 3rd floor was constructed without central columns as this is the top floor and only supporting the weight of the roof. | 22/10/2014 |  | Within 6 weeks. | In Progress

## Fire
Date
14-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Remi Holdings Ltd -Unit 2 (previously A.M.C.S. Textiles Limited), 41 & 52 AEPZ Narayangonj Bangladesh, Narayanganj, Dhaka
Date of Inspection |  | 2014-05-22
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exit stairs are not separated from work areas, on each floor by fire-rated construction. | Provide a minimum 2.0-hr firerated stair enclosure with1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automaticclosing devices tied to the fire alarm system. | Meeting with Accord 23.09.14, further source by certified 3rd party body supplier will need to investigated, More quotes is needed and to look into other materials. Accord will revisit the fty - date to confirm (TBC). 2mths is required to collect all quotations. | Dec 1 2014 | Time extension is only accepted if there is the matter of fire door sourcing & installation. In the meanwhile factory has to ensure the safety of workers. Civil works should be completed within ACCORD timeline (3 months from date report received). The factory has been notified accordingly. | Within 3 months | In Progress
Initial Inspection |  | 2 | Areas used for combustible storage at the ground floor are not separated by fire-rated construction. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Meeting with Accord 23.09.14, further source by certified 3rd party body supplier will need to investigated, More quotes is needed and to look into other materials. Accord will revisit the fty - date to confirm (TBC). 2mths is required to collect all quotations. | Dec 1 2014 | Time extension is only accepted if there is the matter of fire door sourcing & installation. In the meanwhile factory has to ensure the safety of workers. Civil works should be completed within ACCORD timeline (3 months from date report received). The factory has been notified accordingly. | Within 3 months | In Progress
Initial Inspection |  | 3 | The boiler room is not separated by fire-rated construction. Electrical boilers were located at the ground floor without proper firerated separation. | Separate the boiler room by a minimum 1-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Factory will brick close/seal the boiler area and add ceilling. Accord will revisit the fty - date to confirm (TBC). We would like the accord to revisit before commiting to the work. | Dec 1 2014 | Time extension is only accepted if there is the matter of fire door sourcing & installation. In the meanwhile factory has to ensure the safety of workers. Civil works should be completed within ACCORD timeline (3 months from date report received). The factory has been notified accordingly. | Within 3 months | In Progress
Initial Inspection |  | 4 | Unprotected windows are located in front of exterior exit stair. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. | We can brick the front side windows at ground floor as advice. We would like the accord to revisit before commiting to the work. | Dec 1 2014 | Time extension is not accepted. Corrective action plan should be completed within Accord timeline. | Within 3 months | In Progress
Initial Inspection |  | 5 | The exit discharge path serving most exits is less than 10 ft wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft., to provide a minimum 1-hr fire separation. | We can brick up all windows at ground floor along both sides of the building, but the lower ground floor will not have any natural light or natural air. We would like the accord to revisit before commiting to the work. | Feb 1 2015 | Corrective action plan should be completed within agreed timeline | Within 6 months | In Progress
Initial Inspection |  | 6 | Egress gates with locking features are provided at most building exits. All lockable openings were open and unlocked during the inspection. | Remove locking features from all egress gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | As discussed with the Accord 23.09.14, a pocket door can be installed through the Egress gates. Accord will revisit the fty - date to confirm (TBC). 2mths is required to collect all quotations. | Dec 1 2014 | Time extension is not accepted on ACCORD's immediate action. As per ACCORD standard Part6, section 6.8 locking features for all egress doors/gates shall be removed immediately. In the meanwhile if locks are required for security reasons, utilize special door locking features complying with NFPA 101.The factory has been notified accordingly. | Immediately | In Progress
Initial Inspection |  | 7 | Storage was located in the exit stair. Combustible material were located at the bottom of west exit stair. | Remove all storage from exit stairs and egress paths. | As discussed with the Accord 23.09.14, the back exit stairs (under stairs) has no exits and is not a pathway, but all patterns will be removed. | Sep 24 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Immediately | In Progress
Initial Inspection |  | 8 | Sliding gates are provided at most exit discharges and some exit stairs. | Replace all gates along the means of egress with sidehinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | As discussed with the Accord 23.09.14, a pocket door can be installed through the Egress gates. Accord will revisit the fty - date to confirm (TBC). 2mths is required to collect all quotations. | Dec 1 2014 | Time extension is only accepted if there is the matter of fire door sourcing & installation. In the meanwhile factory has to ensure the safety of workers. Civil works should be completed within ACCORD timeline (3 months from date report received). The factory has been notified accordingly. | Within 3 months | In Progress
Initial Inspection |  | 9 | Exit stairs discharge inside the building. Exit stair located at the east side discharge into an open storage area at ground floor. | Provide 2-hr fire-rated exit passageway leading direclty outside. | As discussed with the Accord 23.09.14, creating a passage way will be impossible, as this would change the layout of the approve building plan. Accord will revisit the fty - date to confirm (TBC). To discuss what th minimum requirement to resolve this issue. | Feb 1 2015 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 6 months | In Progress
Initial Inspection |  | 10 | Inspection, testing, and maintenance for the fire alarm system was not in accordance with NFPA 72 | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Documents are updated but Accord to review documents to see what is further required. Accord revisit can varify this has been completed. Visit is TBC. | Dec 1 2014 | Time extension is not accepted. Corrective action plan should be completed within Accord timeline. | Within 3 months | In Progress
Initial Inspection |  | 11 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | As discussed with the Accord 23.09.14, emergency lighting needs to be increase. Documents to be reviewed at revisit. Accord will revisit the fty - date to confirm (TBC). 2mths is required to collect all quotations. | Dec 1 2014 | Time extension is not accepted. Corrective action plan should be completed within Accord timeline. | Within 3 months | In Progress

## Electrical
Date
14-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Remi Holdings Ltd -Unit 2 (previously A.M.C.S. Textiles Limited), 41 & 52 AEPZ Narayangonj Bangladesh, Narayanganj, Dhaka
Date of Inspection |  | 2014-05-22
Finance Plan Agreed
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Oil cup below transformer breather is empty. | Breather oil cup must be filled with transformer oil to required level as instructed by the manufacturer. | Facility management has communicated to the transformer supplier to do a overall servicing which will take a further 15 days to complete. | Oct 7 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 2 | HT cables dropping from OH line, not supported to the pole. | HT cable dropping from HT pole must be protected in steel pipe of required size at least 2m from the ground level to protect the cable from any physical damage. The cablenshould be supported on covered tray or ladder throughout its length up to the HT panel base-plate (except the part of the cable laid underground at a depth of at least 1 meter). | This HT pillar is outside the factory premises, and its repairing or maintenance responsibility is of BEPZA only. The factory management has informed BEPZA who have informed AMCS that it will take another 30 days to complete as they need to reaccess the issue and ensure the cabels are installed securely. | Oct 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 3 | Panel base plates removed to allow cable entry. | Panel base plates must be installed, at all time, and cable(s) entering panel must be firmly fixed with cable gland. | Completed (Attached pics) | Nov 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 3 Months | In Progress
Initial Inspection |  | 4 | Excessive heating of cables inside panel. | Arrange periodic inspection & thermal scan to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. | Completed (Attached pics) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 5 | Barrier/separators between different phases are not installed. | Phase barriers made of non-combustible insulating material preferably rubber between different phases (above 230V) must be installed to prevent flashover. | Factory has completed most of the MDB and SDB boards, Some of the points were missing and facility has fixed all the points. (Completed) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 6 | Multiple cables connected at a terminal of the bus bar. | Remove multiple cables terminating at a terminal in bus bars and terminate single cable at a single point of bus bar. Use pin type bus bar for connecting multiple circuit if the main bus bar does not have enough space. Confirmbreaker the capacity of the bus bar does not get overloaded. | Completed (Attached pics) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 7 | Panel doors not connected with earth bond. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Completed (Attached pics) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 8 | Cable ducts covered with combustible materials | Cable duct should cover with non-combustible material. Maintain cleaning periodically. | WIP - Electrians are working through this and will complete during EID holidays. | Oct 7 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 9 | Instant Power Supply (IPS) batteries placed directly on concrete floor. | Lead acid batteries used for IPS must be placed on acid resistant stands. | Completed (Attached pics) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 10 | Motor in the boiler room, not firmly fixed on the foundation/frame. | Motor in boiler must be firmly grouted on the concrete floor or fixed on the foundation structures. | WIP - Electrians/Builders are working through this and will complete during EID holidays. | Oct 7 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress
Initial Inspection |  | 11 | HT cables laid on concrete floor. | HT cables must be laid in cable trench and supported on cable trays. Existing cable may be protected and supported in cable trays through safe route raised at safe height. | Completed (Attached pics) | Sep 22 2014 | RPO Comments: On 14-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 Month | In Progress