## Structural
Date
26-Feb-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-03-07
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | An expansion at the NW corner of the building for worker latrines was observed during our walk through, and a new fire egress stair was observed at the SW corner of the building. Documentation for these structures were not available for review at the time of our visit. | Have a qualified structural engineer complete an analytical evaluation of the structural impact of the addition. Provide record drawings for these expansions by the engineer of record. A detailed assessment of cantilevered slabs at the NW expansion is required. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 2 | We did not observe special provisions for concentrated loads in the structure. We observed 2000L and 3000L water tanks at the roof top level. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Corrected by ALLIANCE | Jun 30 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. Factory have shifted plastic water tank to another location . On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 3 | Wind and seismic design information not provided on available record documents. | Have a qualified structural engineer document compliance with the seismic and wind requirements stated in the 2006 BNBC. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 4 | Design criteria was not included on available record documents. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 5 | Rooftop cable-stayed antenna and water tanks are not braced for seismic forces. Cable anchors for the antenna were noted to be of poor construction. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 6 | No program was in place at the time of our visit. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 7 | General notes are missing from the structural documents. The design code for the building is not indicated on structural documents. Material strengths used for the design are not indicated on the structural documents. | Provide general notes with design criteria and material strengths from the Engineer of Record. Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20 | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 8 | Exposed reinforcing bars at the NW expansion and roof should be removed and protected from future corrosion. Visible water was noted to be present on the roof that is leaking from rooftop plumbing. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up inspection no water ponding found on the roof. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 9 | As part of the follow up work by EIMS (detailed elsewhere via the column FoS question) conducted following the site visit by Walter P Moore, it was determined that MCAC was used in the construction of the building, including the roof slab. No protective coating was provided at the roof level of the building. | Provide a protective coating at the structural elements constructed with MCAC exposed to rainfall or other sources of water. Have protective coating approved by the Alliance or a qualified structural engineer. | Corrected by ALLIANCE | Jun 30 2015 | On 24/10/2016: During follow up visit it was found protective coating has been provided. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 10 | Certificates of Occupancy were not available at the time of our visit. | Provide Certificates of Occupancy for review. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: As per alliance report,it has been corrected. On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 11 | A designated load manager was not present or on staff at the time of our visit. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: Found corrected by ALLIANCE. On 23-May-2023: Corrected from previous inspection. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 12 | Load Plans were not available at the time of our visit. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3 | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: On 23-May-2023: Corrected from previous inspection. See new findings below. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 13 | Posted load plans were not observed at the time of our visit. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: During follow up visit it was found that load plan for each floor was prepared and posted and loading at all floors were found as per as built load plan. Design report has been approved by Alliance on 03 November 2015. On 23-May-2023: Corrected from previous inspection. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 14 | Load limits in storage areas were not clearly marked. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Corrected by ALLIANCE | May 12 2015 | On 24/10/2016: As per alliance report,it has been corrected. On 23-May-2023: Corrected from previous inspection. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Initial Inspection |  | 15 | Joint between NW expansion and main building is cracking. No expansion joint was provided and the slab at each of these levels has cracked. | Install joint between original building and NW expansion. Remove deteriorated expansion joint material and provide new approved material at the expansion joint. | Corrected by ALLIANCE | Jun 30 2015 | On 24/10/2016: During follow up visit it was found expansion joint has been covered by metal . On 23-May-2023: Corrected from previous inspection. On 13-Aug-2025: Corrected previously. | Jan 31 2015 | Corrected
Follow Up Inspection |  | 16 | New finding-1: Vertical extension of Main Factory Building including adjacent toilet zone part and external steel stair. | Carry out Detail Engineering Assessment (DEA) considering vertical extension of the building. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Jul 4 2023 | .On 23-May-2023: One storey vertical extension observed above existing 4 storied Main Factory Building. The Main building includes adjacent toilet zone part and external steel stair. The factory engineer is required to carry out Detail Engineering Assessment (DEA) of five storied building following BNBC requirements. Please submit the DEA documents to the RSC for review. On 13-Aug-2025: The factory has submitted the revised DEA to RSC. Which is now under review to receive the submission. Progress: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 17 | New finding-2: Vertical extension of Main Factory Building including adjacent toilet zone part and external steel stair. | Revise and actively manage floor loading plan based on foundation, column and floor capacity. | Done | Jul 4 2023 | .On 23-May-2023: One storey vertical extension observed above existing 4 storied Main Factory Building. The factory engineer is required to revise the floor loading plan along with DEA based on foundation, column & floor capacity of current five storied building. During inspection, floor loading was found below 2 kPa on production area and 3 kPa on storage areas. Floor load plan was not found posted to any floor level and storage areas were not designated. However, till acceptance of revised floor load plan by the RSC, post current load plan (2kPa for typical floors & 3 kPa for storage area), designate storage area & height and manage floor loading accordingly. On 13-Aug-2025: The factory has submitted the revised load plan along with DEA to RSC. Which is now under review to receive the submission. During inspecion, floor loading was found with in (2kPa for typical floors & 3 kPa for storage area). Progress: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 18 | New finding-3: Vertical extension of Main Factory Building including adjacent toilet zone part and external steel stair. | Implement required remediation as outcome of DEA. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Nov 23 2023 | .On 23-May-2023: After acceptance of DEA by the RSC, the factory is required to implement the required remediation for the building (including adjacent toilet zone part and external steel stair) within given timeline. On 13-Aug-2025: After receiving EA acceptance from the RSC, the factory is required to carry out remediation works (if any). Progress: 0% | (within 6 months) | In Progress
Follow Up Inspection |  | 19 | New finding-4: Water ponding on the roof; Roof slab made by MCAC have no water proofing layer- Main Factory Building. | Develop water drainage system on the roof and provide water proofing layer on the roof slab with adequate slope. | Done | Jul 4 2023 | .On 23-May-2023: Water ponding observed on the roof slab. The factory is required to develop water drainage system on the roof and provide water proofing layer on the roof slab with adequate slope. On 13-Aug-2025: Sign of water clogging was found on the roof. The factory is required to develop water drainage system on the roof and provide water proofing layer on the roof slab with adequate slope. Progress: 0% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 20 | New finding-5: Dampness throughout the building- Main Factory Building. | Identify the reason of dampness and repair the damp area accordingly. | Done | Jul 4 2023 | .On 23-May-2023: Dampness observed throughout the building. Identify the reason of dampness of slab & wall and repair the damp area accordingly. On 13-Aug-2025: Dampness was observed throughout the building. The factory engineer is required to identify the cause of dampness in the slabs and walls and repair the affected areas using appropriate remedial methods. Progress: 0% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 21 | New finding-6: Potential falling hazard due to lack of stair railing and incomplete parapet wall- Main Factory Building | Provide railing to the open stair and complete parapet wall on the roof. | Done | Jul 4 2023 | .On 23-May-2023: Potential falling hazard observed due to lack of stair railing and incomplete parapet wall on roof. The factory is required to provide railing to the open stair and complete parapet wall on the roof. On 13-Aug-2025: The stair railing and parapet wall have been installed. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 22 | New finding-7: Lack of lateral stability system (missing bracing & compression strut) of Dining Shed | Carry out Engineering Assessment (EA) to confirm the lateral stability of the shed. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Jul 4 2023 | .On 23-May-2023: No bracing & compression strut observed in the Dining Shed. The factory engineer is required to carry out Engineering Assessment (EA) to confirm the lateral stability of the shed and suggest proper remedial actions accordingly. Submit the EA documents to the RSC for review. On 13-Aug-2025: The factory has submitted the revised EA to RSC. Which is now under review to receive the submission. Progress: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 23 | New finding-8: Lack of lateral stability system (missing bracing & compression strut) of Dining Shed | Implement necessary remedial works as outcome of EA. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Nov 23 2023 | .On 23-May-2023: No bracing & compression strut observed in the Dining Shed. After acceptance of EA documents, the factory is required to implement suggested remedial actions. On 13-Aug-2025: After receiving EA acceptance from the RSC, the factory is required to carry out remediation works (if any). Progress: 0% | (within 6 months) | In Progress
Follow Up Inspection |  | 24 | New finding-9: Lack of lateral stability system (missing bracing & compression strut) of Jhut Godown Shed | Carry out Engineering Assessment (EA) to confirm the lateral stability of the shed. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Jul 4 2023 | .On 23-May-2023: No bracing & compression strut observed in the Jhut Godown Shed. The factory engineer is required to carry out Engineering Assessment (EA) to confirm the lateral stability of the shed and suggest proper remedial actions accordingly. Submit the EA documents to the RSC for review. On 13-Aug-2025: The factory has submitted the revised EA to RSC. Which is now under review to receive the submission. Progress: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 25 | New finding-10: Lack of lateral stability system (missing bracing & compression strut) of Jhut Godown Shed | Implement necessary remedial works as outcome of EA. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Nov 23 2023 | .On 23-May-2023: No bracing & compression strut observed in the Jhut Godown Shed. After acceptance of EA documents, the factory is required to implement suggested remedial actions. On 13-Aug-2025: After receiving EA acceptance from the RSC, the factory is required to carry out remediation works (if any). Progress: 0% | (within 6 months) | In Progress
Follow Up Inspection |  | 26 | New finding-11: Lack of documents for the Security Shed & Fire Pump Room | Prepare as-built documents for the structures. | Already DEA re-submitted 10 December-2024,Waiting for RSC approval | Jul 4 2023 | .On 23-May-2023: As-built documents were not available for the Security Shed & Fire Pump Room. The factory engineer is required to prepare as-built documents for the structures. On 13-Aug-2025: The factory has submitted the as-built drawings along with revised DEA to RSC. Which is now under review to receive the submission. Progress: 30% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 27 | New finding-12: Dampness in the concrete slab and roof slab of Fire Pump Room | Investigate the reason & extent of the dampness and repair the damp area following suitable remedial method. | Done | Jul 4 2023 | .On 23-May-2023: Dampness observed in the concrete slab and roof slab of Fire Pump Room. The factory engineer is required to investigate the reason & extent of the dampness and repair the damp area following suitable remedial method. On 13-Aug-2025: Dampness was observed in the concrete slab and roof slab of the Fire Pump Room. The factory engineer is required to investigate the cause and extent of the dampness and repair the affected areas using a suitable remedial method. Progress: 0% | (within 6 weeks) | In Progress

## Fire
Date
26-Feb-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-02-17
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Fire doors are in the process of being installed. | Provide listed outward swinging, fire-rated doors at all openings into stairs and at hazard separation areas. | Corrected | Nov 20 2015 | On 29/05/16: Corrected. Note: If factory wants to keep the door open than factory shall be installed magnetic door holder. If factory uses room for any propose under exit stair, they shall be separated it with fire rated construction. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Re-open. See the issue no. 20 | Dec 31 2014 | Corrected
Initial Inspection |  | 2 | . | Install a Class III standpipe system at required locations. If full automatic sprinkler protection is provided, only a Class I system is needed. Standpipe system must comply with NFPA 14. | Corrected | Nov 30 2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. On 26/09/2021: It is the integrated part of fire protection system. On 23/05/2023: It is the integrated part of fire protection system. | Dec 31 2014 | Corrected
Initial Inspection |  | 3 | There were unprotected penetrations through the floor at each electrical cabinet location. Additionally, the fire sprinkler risers need to be protected at the floor openings. | Provide fire-resistive rated opening or penetration protection for rated walls and assemblies in accordance with Alliance Standard Sections 4.6 and 4.7. Consult a qualified fire protection engineer to design the required opening protectives or penetration systems. | Corrected | Jun 30 2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. On 23/05/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 4 | Automatic protection systems being installed. | Install a dedicated fire pump for the facility in accordance with NFPA 20. Also, install a water storage tank in accordance with NFPA 22. Submit plans of under construction system to Alliance for review. | Corrected | Nov 30 2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. On 26/09/2021: It is the integrated part of fire protection system. On 23/05/2023: It is the integrated part of fire protection system. | Dec 31 2014 | Corrected
Initial Inspection |  | 5 | Fire alarm panel does not report to a central facility. Additionally, the fire pump is not monitored by the fire alarm panel. | Arrange for direct connection of the fire alarm and detection system to a central station monitoring service or the Fire Service and Civil Defence per Alliance Standard Part 5 Section 5.7.5 Monitoring. Until that time that a central station monitoring service or direct connection to the Fire Service and Civil Defence can be set up, a person trained to contact the Fire Service and Civil Defence in the event of fire alarm activation shall be provided. An annunciator shall be located in a constantly attended location (such as a fire control room) to alert this person. Have the fire pump conditions monitored by the fire alarm panel in accordance with NFPA 20. | Corrected | Jun 30 2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Issue reopened. On 26/09/2021: It is the integrated part of fire alarm system. On 23/05/2023: It is the integrated part of fire alarm system. | Dec 31 2014 | Corrected
Initial Inspection |  | 6 | Battery exit lighting is provided | Install emergency lighting for all paths of egress in accordance with Alliance Standard Section 6.7. | Corrected | Jun 30 2015 | On 29/05/16: Corrected. As per Alliance last follow-up report this issue has been corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. Issue reopened. | Dec 31 2014 | Corrected
Initial Inspection |  | 7 | Handrails are provided on one side of the stair only. | Provide handrails on both sides of each stairway. Mount handrails at a height between 30 in. and 44 in. | Corrected | May 29 2016 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. On 23/05/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 8 | Exit signs are provided at the stairs. | Provide continuously illuminated exit signs per Alliance Standard Section 6.11. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. | Corrected | Dec 5 2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. Issue reopened. | Dec 31 2014 | Corrected
Initial Inspection |  | 9 | Occupant load signage is not provided. | Post the occupant load for all assembly and production floor areas in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Dec 5 2015 | On 29/05/16: Corrected. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. On 23/05/2023: Corrected. | Dec 31 2014 | Corrected
Initial Inspection |  | 10 | No certificate of occupancy provided for review. | Obtain the the Certificates of Occupancy for each building and ancillary structure according to building use from the approving authority. | Corrected | Dec 5 2015 | On 29/05/16: Not applicable. On 01/09/16: Not applicable. On 13/08/17: Not applicable. On 20/11/2017: Corrected. N/A. On 26/09/2021: Corrected. On 23/05/2023: Corrected. | Dec 31 2014 | Corrected
Follow Up Inspection |  | 11 | The egress path along means of egress has interrupted by obstruction/storage. | Means of egress shall be maintained continuously free and clear of all obstructions/storage. Or Keep egress paths and stairs clear of storage. | Corrected | Sep 6 2016 | On 29/05/16: New Finding. On 01/09/16: Corrected. On 13/08/17: Corrected. On 20/11/2017: Corrected. On 26/09/2021: Corrected. On 23/05/2023: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 12 | New Finding (4th FU): Heavy fire load has been observed at the production floors due to the presence of large area of unenclosed combustible storages. | Provide defined storage areas and limit the storage arrangement as Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | We have already started the works It will finished to March 23,2023 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: In progress. It has been found same as it was before. (RCH) Comments:02-Mar-2023: Factory asked time extension , which is not accepted. Remediation work must be completed as per approved timeline. On 23/05/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 13 | New Finding (4th FU): Staff dinning at ground floor was observed inside the store room. | Remove dinning from the location Or Provide 3-hr fire separation with direct exit discharge. | Done | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: In progress. It has been found same as it was before. On 23/05/2023: Corrected at the store room on the ground floor, but the same is required to be separated at the dining shed at the east side of the building. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 14 | New Finding (4th FU): The exit discharge path from store and other areas at ground floor is less than 10 ft. wide and is not separated from the building interior. | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 1-hr fire separation. | We have already sealed all the intrusions inside the building along the discharge path, up to 10 feet height, with brick. | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: In progress. It has been found same as it was before. On 23/05/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 15 | New Finding (4th FU): Storage was located in the exit stair enclosure. | Remove all storage from exit stairs. | We have already started the works It will finished to March 06,2023 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: Installed fire rated door but door coordinator is not working properly. (RCH) Comments:02-Mar-2023:Factory asked time extension , which is not accepted. Remediation work must be completed as per approved timeline. On 23/05/2023: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding (4th FU): Proper third party certification for fire pump was not available. | Provide proper third party certification for fire pump. | We have already In-house UL Listed Fire Pump, will send you after getting the third party certificate 03 January,2025 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: It is an integrated part of fire protection system. On 23/05/2023: The factory submitted the drawing to the RSC for review. The fire pump room and water reservoir construction shall be started. New pump procurement shall be started accordingly. RPO Comments: On 02-Dec-2024 the factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 17 | New Finding (4th FU): During inspection it was observed that the auto-start for the fire pumps were non-functional. | Install fire pump as per NFPA-20 | We have started the work of civil walk and when the work is completed we will install the pump on January 30, 2025 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: It is an integrated part of fire protection system. On 23/05/2023: The factory submitted the drawing to the RSC for review. The fire pump room and water reservoir construction shall be started. New pump procurement shall be started accordingly. RPO Comments: On 02-Dec-2024 the factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 18 | New Finding (4th FU): Installed stand-pipe system were not as per NFPA-14. | Provide standpipe and hose system as per NFPA 14 & 20. | Pipe work will be completed with fire pump work. We will finished on January 30, 2025 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: Still design is not submitted to the RSC. On 23/05/2023: The factory submitted the drawing to the RSC for review. The fire pump room and water reservoir construction shall be started. New pump procurement shall be started accordingly. RPO Comments: On 02-Dec-2024 the factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 19 | New Finding (4th FU): Installed Fire alarm system were observed not as per NFPA-72. Battery were undersized, No supervision for Sounders were observed. | Modify the current addressable fire alarm system in accordance with NFPA 72. | We have done Fire alarm LC.We will finished the work 30 January, 2025 | Dec 21 2017 | On 20/11/2017: New Finding On 26/09/2021: Design has been submitted to the RSC to review. On 23/05/2023: The factory submitted the drawing to the RSC for review. RPO Comments: On 02-Dec-2024 the factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress
Follow Up Inspection |  | 20 | New Finding (5th FU): Exit stair shall seperated with production floor by listed fire rated door. | Provide listed outward swinging, fire-rated doors at all openings into stairs and at hazard separation areas. If fire doors need open always then provide magnetic door holder & interfaced with FACP. | Done | Nov 26 2021 | On 26/09/2021: New Findings On 23/05/2023: Non fire-rated door is required to be removed. Interfacing is done at almost all the locations. Fire rated doors have not been interfaced on the ground floor. Unapproved means have been found at place to keep the door open. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 month | Pending Verification
Follow Up Inspection |  | 21 | New Finding (5th FU): Adequate emergency light need to provide | Install emergency lighting for all paths of egress in accordance with RSC Standard. | We have already installed emergency lighting for all exits as per RSC standard. | Oct 26 2021 | On 26/09/2021: New Findings On 23/05/2023: Additional emergency light were provided but still inadequate on the 2nd floor. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 22 | New Finding (5th FU): Directional signs need to provide. | Directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious. | Already we have started the work of directional signs it will take time to complete 30th January, 2025 | Oct 26 2021 | On 26/09/2021: New Findings On 23/05/2023: Provided at some locations but still inedequate. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 month | Pending Verification
Follow Up Inspection |  | 23 | New Finding (5th FU): Stair designation sign | Stair designation signs shall be provided at each floor entrance from the stair to the floor in English and Bengali. Signs shall indicate the name of the stair and the floor level. Signs shall be posted adjacent to the door. | We have already started the work and Stair Designation signs will be provided.It will fnished to 09 March, 2023 | Oct 26 2021 | On 26/09/2021: New Findings (RCH) Comments:02-Mar-2023:Factory asked time extension , which is not accepted. Remediation work must be completed as per approved timeline. On 23/05/2023: Corrected. | Within 1 month | Corrected

## Electrical
Date
26-Feb-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Sawftex Ltd, Bhangnahati, Sreepur, Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-06-29
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Workers that operate and maintain the electrical system have not received electrical safety training. | Develop and implement an electrical safety program. Include key topics such as lock out tag out procedures, personal protective equipment requirements, etc. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 2 | Distribution boards are metal enclosed with no dead front construction. | Ensure distribution boards are metal enclosed with a dead front construction. | Corrected | Jun 30 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 3 | Underground service cables are laid in non-conformity with the requirements of concealed wiring. | Ensure underground cables for electrical distribution in the premises, garden, compound of the building are encased in GI or pvc pipes and laid in earth trenches of sufficient depth as per BNBC. | Corrected | Dec 5 2015 | On 29/05/2016: Underground service cables are found concealed. | Apr 24 2015 | Corrected
Initial Inspection |  | 4 | Cable trenches are not covered properly. | Provide adequate cover on cable trench. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 5 | Emergency power distribution boards are available but not properly identified. | All boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits shall be permanently marked so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 6 | The substation room has no required fire rating or protection but is physically separated from the remainder of the building. | Provide adequate fire rating, protection for substation room. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. Physically separated with fire door. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 7 | No additional insulation is provided for wiring exposed to external heat sources. | In order to avoid the effects of heat from external sources one of the following methods should be used to protect wiring systems: (1) shielding; (2) placing 900 mm (36 in.) from the source of heat; (3) local reinforcement or substitution of insulating material. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 8 | Indications of overheating were observed in 72.1°C. Note: Detail thermography report is uploaded here under general information section. | Find out the cause of overheating and take proper action including replacing cable or equipment where necessary. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 9 | Bunch of cables observed at circuit breakers within distribution boards. | Remove bunch of cables at circuit breakers within distribution boards. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 10 | Distribution boards are not provided with a minimum clearance of 1 m (39 in) in front. | Provide clearance of at least 1 m (39 in) in front of distribution boards. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 11 | Proper working or “as built” electrical diagram of main distribution circuit and floor levels circuits connecting electrical loads (machines/lights/cooling system etc.) are not available at site. The provided single line diagram was as built but no electrical layout drawing found. | Have a qualified electrical engineer develop an as-built single line diagram detailing key components and capacity of the electrical system. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 12 | Thermo graphic scans of electrical equipment have not been done. | Complete thermo graphic scans at least on a three year cycle. Thermo graphic scans should be completed in accordance with the standard for Infrared Inspection of Electrical Systems & Rotating Equipment. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 13 | No periodic safety inspections of the electrical system components is completed. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 14 | No such information and documents found to verify the existence of harmful substances such as PCBs in transformer. | Consider replacing transformers that contain harmful substances to reduce health hazards. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 15 | Distribution boards have no capacity information labels. A capacity information is provided in all distribution boards which is inadequate due to not covering all the required information. There is no indication of voltage & current capacity of the panel. | Provide capacity information labels (maximum current rating, no of circuit breakers etc.) for distribution boards. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 16 | Distribution boards are not provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Ensure distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 17 | Electrical cables are not properly identified. | Ensure the means of identification is obtained by separate color coding, marking tape, tagging, or other approved means. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 18 | Each circuit is not provided with a dedicated neutral. There is no marking of neutral cable in the panel. | Provide marking of neutral cable & ensure dedicated neutral for each circuit. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 19 | Mechanical guards are not provided for electrical equipment. Change over switch is placed on the floor without any protection in substation room. | Provide mechanical guards for electrical equipment where necessary. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 20 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Ensure lightning protection ground terminals are bonded to the building or structure grounding. | Corrected | Feb 12 2015 | On 29/05/2016: Building structure was found bonded to the lightening protection ground terminal. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 21 | The substation room has improper illumination. | Provide additional light fixtures to increase illumination levels provided in the BNBC. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 22 | The substation room is not secured properly. | Install security measures to ensure access to the substation is restricted. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 23 | Improperly stored combustible material found beside generator. | Remove all dirt, debris, lint, water, oil, and improperly stored materials from the substation room. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 24 | The substation room has inadequate ventilation. There is a single exhaust fan provided but no means for cross ventilation. | Provide means of ventilation for the substation room. Consult a qualified electrical engineer to determine the required ventilation rates based on the installed equipment. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 25 | Cable sockets are not provided for stranded conductors. | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. Conductors below 6 mm2 without cable sockets, all strands at the exposed ends are soldered together or are crimped using suitable sleeve or ferrules. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 26 | Improper cable joints were found. | Ensure cable joints through porcelain, pvc connectors with PIB tape wound around joint. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 27 | The electrical switchgear and panel boards are not inspected on an annual basis to ensure that the equipment is installed in accordance with the listed ratings. A checklist of inspection is maintained for all electrical switchgear and panels which is inadequate due to not covering all the required information. | Inspect electrical switchgear and panel boards on an annual basis to ensure that the equipment is in good working condition. | Corrected | Jun 30 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 28 | Generator frame earthing is not provided at two separate points. Single point earthing is provided. | Provide two separate points frame earthing for generator. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 29 | No periodical Insulation Resistance measurement program established. A record of insulation resistance test found conducted by the factory owned machine. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). All transformers, switchgears etc. shall be subject to an insulation resistance measurement test to ground after installation but before any wiring is connected. Insulation tests shall be made between open contacts of circuit breakers, switches etc. and between each phase and earth. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 30 | Internal components of distribution boards are not properly concealed. Panel bottom has opening in SDB/Dinning Room, Ground Floor. | Provide covers or blanks to conceal all live internal components of switchboards and/or distribution boards. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 31 | Electrical cable is not properly terminated. | Ensure all electrical cable properly terminated at its point of termination. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 32 | Electrical connections at fixtures are not properly secured. | Ensure electrical connections at equipment, fixtures, etc. are properly secured. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 33 | Junction boxes are not provided with adequate covers. | Provide adequate covers for junction boxes and other electrical devices. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. No such issue has been found during follow-up inspection. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 34 | Electrical wiring and conduit is not properly supported. | Provide adequate supports for electrical wiring and conduit. | Corrected | Feb 12 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 35 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Light fixtures without protective covers (otherwise known as naked lights) shall not be allowed in storage areas or in any area where the Inspector of the factories rules disallows these fixtures. Install signs posted in Bengali and English, indicating this prohibition at all entrances to these areas. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 36 | Transformer oil analysis is not completed on main service transformers. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 37 | Equipment safety signage is not posted within the room properly. | Indoor electrical installations that are accessible to unqualified persons shall be made with metal-enclosed equipment. Switchgear, unit substations, transformers, pull boxes, connection boxes, and other similar associated equipment shall be marked with appropriate caution signs. Entrances to rooms and other guarded locations that contain exposed live parts shall be marked with conspicuous warning signs forbidding unqualified persons to enter. Caution, warning, danger signs or labels should meet the following requirements: (1) The marking shall adequately warn of the hazard using effective words and/or colors and/or symbols. American National Standards Institute ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for suitable font sizes, words, colors, symbols, and location requirements for labels. (2) Shall be permanently affixed to the equipment or wiring method and shall not be hand written. Exception, portions of labels or markings that are variable, or that could be subject to changes, shall be permitted to be hand written and shall be legible. (3) The label shall be of sufficient durability to withstand the environment involved. ANSI Z535.4-2011, Product Safety Signs and Labels, provides guidelines for the design and durability of safety signs and labels for application to electrical equipment. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 38 | Phase separators are not provided between terminals on circuit breakers. | Install phase separators between terminal connections. Verify phase separators are installed at all remaining locations. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Initial Inspection |  | 39 | Inspection, maintenance being completed but testing procedures of the emergency generator are not being completed. | Establish a routine maintenance and testing program for the emergency generator. The program shall be based on all of the following: (1) Manufacturer's recommendations. (2) Manufacturer's Instruction manuals. | Corrected | Dec 5 2015 | On 29/05/2016: Corrected. On 01/09/2016: Found corrected on 1st follow-up. Also found corrected in the second. | Apr 24 2015 | Corrected
Follow Up Inspection |  | 40 | New Finding: Portable generator is being used for uncertain time in a unsafe way and is placed near the main exit of the factory. | Portable generator and its accessories shall be placed at a safe location to minimize hazard and the conductors for power distribution shall be protected. | Corrected | Nov 15 2016 | On 13/08/2017: Not corrected. On 20/11/2017: Corrected. Portable generator has removed. | 2 Weeks | Corrected
Follow Up Inspection |  | 41 | New Finding: Air terminal are missing at several points of Lightning Protection System and baseplate is inadequate. | Missing air terminals shall be reinstalled and baseplate should be as per standard. | Remediation work is completed | Dec 25 2017 | On 10/10/2021: Not corrected. Complete the remediation work following NFPA 780. Calculate risk index for dinning shed and install LPS according to that. On 23/05/2023: Not corrected. Factory has started 4th floor extension work. That's why the whole LPS system was kept open on the roof top. On 18/02/2024: Not corrected. 4th floor extension is completed. The factory is working to re-design LPS and install accordingly. On 19/08/2024: Not corrected. The factory has redesigned the LPS system, but installation is not yet complete. On 11/08/2025: Not corrected. No significant progress has been observed. During the inspection, LPS installation has been found partially completed for Building-1. But the other structures have been found without any LPS installation. RPO Comments: On 25-Feb-26 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 42 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator shall be 1.07 m. If multiple generators are installed, the gap between two generators must be equal to the width of the bigger one. |  | Dec 25 2017 | On 10/10/2021: Not corrected. Prepare a layout for the remediation and then do the renovation work. On 23/05/2023: Not corrected. No progress has been observed. Clearance required for both transformer & generators. On 18/02/2024: Corrected. Adequate space is available around generator. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | Cable ducts must be properly sealed to avoid ingression of any foreign particles. |  | Dec 25 2017 | On 10/10/2021: Not corrected. Cover the cable duct and keep the trench/duct clean. On 23/05/2023: Not corrected. Some progress has been observed. But still found some cable channel left open. On 18/02/2024: Not corrected. Significant progress observed. Cable channel opening observed at few places. On 19/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 44 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200 mm above floor level. | Done | Dec 25 2017 | On 10/10/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Safety program is initiated but has no influence in the factory. | Electrical safety training and awareness program for the electrical personal and workers must be conducted and recorded. Training must have an impact on the safety attitude of the personnel. | Already we have done third party electrical training. | Dec 25 2017 | On 10/10/2021: Not corrected. Factory has initiated the training programmed. Need to arrange insulated PPE and LOTO. On 23/05/2023: Not corrected. No progress has been observed. On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Power cables entering or exiting from distribution board/panel are not properly fixed. | Power cables entering or exiting from distribution board/panel must be fixed through panel base/top plate using proper sized cable glands (metal/pvc). |  | Dec 25 2017 | On 10/10/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | Dec 25 2017 | On 10/10/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Transformer body earthing (equipment earthing) and neutral earthing (System earthing) cable size is inadequate. Inadequate sized earth cable connected to generator frame. | Equipment earthing cable size must be increased. The earth cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. Two separate earth connection & one separate and distinct neutral connection must be provided over generator. Generator body must have earth connection with half of phase conductor. |  | Dec 25 2017 | On 10/10/2021: Not corrected. On 23/05/2023: Not corrected. No progress has been observed. On 18/02/2024: Not corrected. Significant progress observed. The factory has constructed new earth pits for transformer which found adequate. But Ecc cable size is inadequate. On 19/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: Transformer silica gel is discolored. | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | done | Dec 25 2017 | On 10/10/2021: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Generator output cables (laid on floor) are not protected and supported. | Service cables from generator must be supported at its own breaker's terminal and with cable tray. | We are transfer the Electrical substation in RMG Predecease will finish the work 20 February, 2024 | Dec 25 2017 | On 10/10/2021: Not corrected. Cable must be supported and protected adequately. On 23/05/2023: Not corrected. No progress has been observed. On 18/02/2024: Not corrected. The Diesel generator output power cables are laid on floor. On 19/08/2024: Corrected. The generator room has been demolished, and no generator is currently in use. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: No working separation between LT (Low Tension) panel/s and HT (High Tension) unit/s (transformer, HT switchgear) and there is no proper access to transformer. | A working separation between LT and HT must be ensured. A brick wall will do it; and adequate working clearance (1.07 m) and ventilation must be ensured. Proper access to the transformer should ensured for maintenance. | Our electrical team Starting the works. We will finished the work 20 th February, 2024. | Dec 25 2017 | On 10/10/2021: Not corrected. On 23/05/2023: Not corrected. No progress has been observed. On 18/02/2024: Not corrected. Significant progress has been observed. The factory has relocated the substation and working to remediate the issue. On 19/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Thermography scanning report is outdated. | Thermography survey must be done and recorded at least twice in a year. |  | Nov 20 2021 | On 23/05/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Earth pit resistance record is unavailable. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. |  | Nov 20 2021 | On 23/05/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Transformer oil test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. |  | Nov 20 2021 | On 23/05/2023: Not corrected. Factory has done the oil test but the oil condition is not good according to test report. Change the oil or centrifuge it. Then check the transformer oil condition by performing oil test. On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Transformer breather oil cup is empty. | Transformer breather oil cup must be filled up to the oil mark on the cup. |  | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Equipment earth cable (for generator) size is inadequate. | At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. |  | Jun 29 2023 | On 18/02/2024: Not corrected. Generator body earthing provided from single pit. Also earth electrode size is inadequate (6 mm). On 19/08/2024: Corrected. The generator room has been demolished, and no generator is currently in use. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be cleaned. |  | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Generator terminal box left open to allow cable entry. | Base plate for generator terminal box must be installed and cables entering terminal box must be firmly fixed with cable gland. | Because we have separated all the electrical lines of RMG section. We will finished the works 20 Febuary,2024. | Jun 29 2023 | On 18/02/2024: Not corrected. Diesel Generator output terminal box left open. On 19/08/2024: Corrected. The generator room has been demolished, and no generator is currently in use. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Heat shields/blankets missing to protect component and operator from excessive heat. | Heat shields/blankets must be installed to shield hot surface to protect component and operator from excessive heat. Proper guards shall be provided after shielding hot surface. Blankets on exhaust manifold, turbocharger housing and other engine components is not necessary. Suggested to consult with the generator supplier /service provider/expert before doing the job. |  | Jun 29 2023 | On 18/02/2024: Not corrected. No progress has been observed. On 19/08/2024: Corrected. The generator room has been demolished, and no generator is currently in use. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding: Earth pits are not identifiable properly. | Each earth pit shall be properly identifiable and marked for periodic maintenance. | Because we have separated all the electrical lines of RMG section. We will finished the works 20 Febuary,2024. | Jun 29 2023 | On 18/02/2024: Not corrected. Earth pits are not identified at several places. On 19/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Individual overload protection missing for motor above 376 W. | Every electric motor having a rating exceeding 0.376 kW shall be provided with individual control equipment incorporating means of protection against overcurrent. | Done | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Combustible material attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from combustible materials. | Done | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Done | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Cable tray is overloaded with excessive cables. | Proper sized cable tray must be installed; a perforated one is better and 20-25% space in cable tray/duct shall be kept free. | Because we have separated all the electrical lines of RMG section. We will finished the works 20 February, 2024. | Jun 29 2023 | On 18/02/2024: Not corrected. Observed at LT and MDB panels. The factory is re-arranging the panels. On 19/08/2024: Corrected. The generator room has been demolished, and no generator is currently in use. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Because we have separated all the electrical lines of RMG section. We will finished the works 20 February, 2024. | Jun 29 2023 | On 18/02/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. |  | Apr 25 2024 | On 19/08/2024: Not corrected. SLD has not been submitted yet. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Not corrected. SLD was "Accepted" by RSC on Sep'2024. Approximately 40% progress has been observed. However, several issues have been identified, including non-availability of as-built SLD, mismatches in earthing layout, missing earth pit and cable identification, mismatches in circuit breaker ratings and adjustments, load identification mismatches, missing individual protection etc. | 2 Months | In Progress
Follow Up Inspection |  | 67 | New Finding: Circuit breaker installed without any enclosure. | Each MCCB/ MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. |  | Mar 25 2024 | On 19/08/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Panel/distribution boxes are inaccessible. | Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2 m from base; and door opening shall be at least 90 degree. | Done | Mar 25 2024 | On 19/08/2024: Not corrected. In the generator room, inaccessible panels were removed and a new panel was installed below 0.45 m above the floor. RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record. Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Done | Sep 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Done | Sep 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Circuit breaker has no capacity information. | Each circuit breaker must have its own capacity information. | Done | Sep 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Distribution board's top/bottom is left open (typical issue). | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Gland shall be used, where required. |  | Oct 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Not corrected. This issue is still found during inspection. | 2 Months | In Progress
Follow Up Inspection |  | 73 | New Finding: Phase barrier/separators are missing in MCCBs. | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it). | Done | Oct 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 74 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Done | Oct 29 2024 | RPO Comments On 02-Dec-2024: the factory management reported the remediation completion. This item will be verified in the next inspection. On 11/08/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 75 | New Finding: Periodicity of Transformer Oil Test (dielectric strength) survey is not continued. | Testing of transformer oil, specifically the dielectric strength test needs to be conducted at least once in a year from government-authorized entities such as BPDB, BREB, PGCB, EGCB, DESCO, DPDC, or any other designated govt. authority. |  | Sep 11 2025 | RPO Comments: On 24-Aug-25 the factory management is on track with the remediation | 1 Month | In Progress
Follow Up Inspection |  | 76 | New Finding: Outdoor cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. |  | Oct 11 2025 | RPO Comments: On 24-Aug-25 the factory management is on track with the remediation | 2 Months | In Progress
Follow Up Inspection |  | 77 | New Finding: Power cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor cables must be covered, if required. |  | Oct 11 2025 | RPO Comments: On 24-Aug-25 the factory management is on track with the remediation | 2 Months | In Progress