## Structural
Date
15-Mar-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Taratex Fashion Limited, 6/1, Naimuddin Mollah Road, North Augh Para, Tongi Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-08-17
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Capacity check of roof slab supporting water tanks. | Factory Engineer to survey the actual conditions and revise the drawings. | Corrected, dated on 28 Nov-2016 Accord has reviewed & accepted our DEA report &We have submitted revised DEA to Accord on 21 August 2017. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: Previous timeline: 30.12.15 This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. The factory person was asked to submit the EA within 18.02.16. On 20 April 2017: A set of as built drawing was produced by factory engineer and submitted to ACCORD along with DEA report. Factory has carried out Detail Engineering Assessment(DEA). DEA has reviewed and accepted by Accord. During verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: As built drawing has been produced and covered in DEA. DEA has been re-accepted on 28th Nov-2017. On 04th July 2018: Corrected from previous inspection. As-built drawing has been revised and re-accepted on 28th Nov-2017. On 19-Sep-2021: This issue was corrected from previous inspection. A set of as built drawing for 6 storied RCC building was produced by factory engineer and submitted to ACCORD along with DEA report which was re-accepted from ACCORD on 28 November 2017. On 28-Oct-2024: Corrected previously. | within 6 – weeks | Corrected
Initial Inspection |  | 2 | Inadequacies between the drawing and the actual as-built conditions. | Any results of the Engineering Assessment which affect the structure should be taken on board. | Corrected. Revised EA is Accepted by Accord, Retrofiting work is done at 5 colum and this work is 100% completed. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: Previous timeline: 30.12.15 This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. The factory persons was asked to submit EA within 18.02.16 On 20 April 2017: Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. As per accepted DEA recommendation, factory has carried out strengthen works. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: As per re-accepted DEA some columns were required to be retrofitted within 28th January 2017 but during inspection it was observed that factory has not started the retrofitting work. Factory must complete the retrofitting works. On 04th July 2018: Some columns retrofitting were required according to the re-accepted DEA. During inspection all retrofitting works were found completed. Factory management provided the construction completion certificate by the consultant. On 19-Sep-2021: This issue was corrected from previous inspection. Factory has carried out DEA report for 6 storied RCC building, which was re-accepted by ACCORD on 28 November 2017. As per re-accepted DEA recommendation, factory has completed all strengthen works. On 28-Oct-2024: Corrected previously. | within 6 – weeks | Corrected
Initial Inspection |  | 3 | Inadequaciesnbetween the drawing and the actual as-built conditions. | Continue to implement load plan. | Corrected. Revised EA is Accepted by Accord, Retrofiting work is done at 5 colum and this work is 100% completed. | Apr 30 2016 | On 6-Jul-15: Factory management have submitted the DEA that is under review. It is recommended that they have to maintain load according to the loading plan suggested by the factory engineer On 14-feb-2016: Previous timeline: 30.12.15 This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. The factory person was asked to submit EA within 18.02.16 On 20 April 2017: Load plan was produced along with DEA. Load plan found posted. During inspection load was found above allowable loading limit at 1st floor finished goods area. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. As per accepted DEA recommendation, factory has carried out strengthen works. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: Factory shall be able to implement final load plan after completion of retrofitting works. Meanwhile they have to maintain the intermediate load plan. On 04th July 2018: Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 19-Sep-2021: This issue was corrected from previous inspection. Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 28-Oct-2024: Corrected previously. During inspection, load plan found posted in each floor and loading found as per accepted final load plan (42psf). | within 6-months | Corrected
Initial Inspection |  | 4 | Capacity check of roof slab supporting water tanks. | Factory Engineer to review design, loads and related elements in area identified above to confirm capacity for these items. Or | Corrected on 2nd follow-up inspection. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: During inspection we found that the roof slab is removed. On 20 April 2017: 11 nos. plastic water tank found on roof top which was incorporated in DEA. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. Remediation works of this factory has carried out, as per accepted DEA recommendation. Also RCC overhead water tank found removed. On 27th Dec 2017: Corrected from previous inspection. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. During inspection 3 nos plastic water(5000 litter per tank) tank was found at roof floor. Also RCC overhead water tank found removed. On 28-Oct-2024: Corrected previously. | within 6 – weeks | Corrected
Initial Inspection |  | 5 | Capacity check of roof slab supporting water tanks. | • The items in the area identified above should be removed. | Corrected, dated on 28 Nov-2016 Accord has reviewed & accepted our DEA report. & We have submitted revised DEA to Accord on 21 August 2017. | Apr 30 2016 | On 20 April 2017: 11 nos. plastic water tank found on roof top which was incorporated in DAE. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. Remediation works of this factory has carried out, as per accepted DEA recommendation. Also RCC overhead water tank found removed. On 27th Dec 2017: Corrected from previous inspection. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. During inspection 3 nos plastic water tank(5000 litter per tank) was found at roof floor. Also RCC overhead water tank found removed. On 28-Oct-2024: Corrected previously. | within 6 – weeks | Corrected
Initial Inspection |  | 6 | No loading plans exist for the structure. | An Engineering Assessment is required to review the design and loads. | Corrected, dated on 28 Nov-2016 Accord has reviewed & accepted our DEA report. & We have submitted revised DEA to Accord on 21 August 2017. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: Previous timeline: 30.12.15 This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. During inspection we found more than 42 psf in various places of different floors. The factory person was asked to follow the initial inspection report and maintain the minimum floor load before getting the approval of the load plan The factory person was asked to submit EA within 18.02.16 On 20 April 2017: Load plan was produced along with DEA. During inspection load was found above allowable loading limit at 1st floor finished goods area. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 04th July 2018: Corrected from previous inspection. Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 19-Sep-2021: This issue was corrected from previous inspection. Factory has carried out DEA report for 6 storied RCC building, which was re-accepted by ACCORD on 28 November 2017. As per re-accepted DEA recommendation, factory has completed all strengthen works. On 28-Oct-2024: Corrected previously. During inspection, load plan found posted in each floor and loading found as per accepted final load plan (42psf). | within 6 – weeks | Corrected
Initial Inspection |  | 7 | No loading plans exist for the structure. | Factory Engineer to state the maximum weight that is allowed per square meter. State the values clearly on notice boards in these areas. (Loading Plans). | Corrected. Load plan is posted at all necessay points and maintaining accordingly. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. During inspection we found more than 42 psf in various places of different floors. No loading plan was shown. The factory person was asked to follow the initial inspection report and maintain the minimum floor load before getting the approval of the load plan. The factory person was asked to submit EA within 18.02.16 On 20 April 2017: Load plan was produced along with DEA. During inspection load was found above allowable loading limit at 1st floor finished goods area. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: Load plan has been produced as a part of DEA and accepted from Accord. During inspection load plan was found posted in every floor and load was below allowable limit. Load marking was observed in the storage areas. Final load plan will be followed after completion of retrofitting works. On 04th July 2018: Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 19-Sep-2021: This issue was corrected from previous inspection. Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 28-Oct-2024: Corrected previously. During inspection, load plan found posted in each floor and loading found as per accepted final load plan (42psf). Load height marking was observed in storage area. | within 6 – weeks | Corrected
Initial Inspection |  | 8 | No loading plans exist for the structure. | Maintain standards of quality control to ensure that storage procedures are correctly followed. | Corrected. Load plan is posted at all necessay points and maintaining accordingly. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. It is recommended that they should follow the storage procedures suggested by the factory engineer. On 14-feb-2016: This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. During inspection we found more than 42 psf in various places of different floors. On 20 April 2017: Load plan was produced along with DEA. During inspection load was found above allowable loading limit at 1st floor finished goods area. Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: Load plan has been produced as a part of DEA and accepted from Accord. During inspection load plan was found posted in every floor and load was below allowable limit. Load marking was observed in the storage areas. Final load plan will be followed after completion of retrofitting works. On 04th July 2018: Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 19-Sep-2021: This issue was corrected from previous inspection. Load plan was produced as part of DEA and accepted by ACCORD. During inspection after retrofitting load plan was found posted. Load was found below 42 psf at every floor. On 28-Oct-2024: Corrected previously. During inspection, load plan found posted in each floor and loading found as per accepted final load plan (42psf). | within 6-months | Corrected
Initial Inspection |  | 9 | Overall stability system | An Engineering Assessment of the overall building to be carried out and in particular, stability and foundation aspects should be investigated in detail. | EA Assessment is done. | Apr 30 2016 | On 6-Jul-15: This part will be covered by DEA. They have submitted the DEA that is under review. On 14-feb-2016: Previous timeline: 30.12.15 This part will be covered by Engineering Assessment. We already reviewed the EA report and the factory was requested to submit the revised EA report within 5.01.2016. The factory persons tell that they will submit EA within 18.02.16 On 20 April 2017: Factory has carried out Detail Engineering Assessment(DEA). DEA has accepted by Accord. Remediation works of this factory has carried out, as per accepted DEA recommendation. However during verification, some mismatch was found. Factory is required to submit the revised as built drawing with DEA. On 27th Dec 2017: As per re-accepted DEA some columns were required to be retrofitted within 28th January 2017 but during inspection it was observed that factory has not started the retrofitting work. Factory must complete the retrofitting works. On 04th July 2018: Some columns retrofitting were required according to the re-accepted DEA. During inspection all retrofitting works were found completed. Factory management provided the construction completion certificate by the consultant. On 19-Sep-2021: This issue was corrected from previous inspection. Factory has carried out DEA report for 6 storied RCC building, which was re-accepted by ACCORD on 28 November 2017. As per re-accepted DEA recommendation, factory has completed all strengthen works. On 28-Oct-2024: Corrected previously. | within 6 – weeks | Corrected
Initial Inspection |  | 10 | No waterproofing materials. | Waterproofing on the roof slab is to be applied. Moreover the roof slab drainage system should be investigated and improved. | Corrected on 2nd follow-up inspection. | Apr 30 2016 | On 6-Jul-15: No water proofing material is installed yet. On 14-feb-2016: Previous timeline: 30.12.15 During inspection we found almost 50% work is done. The Factory person told they need 40 days to complete the full job. Previous time line was 30.12.15 On 20 April 2017: During inspection water proofing work found complete. On 27th Dec 2017: Corrected from previous inspection. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. Factory has provided water proofing layer at roof floor. On 28-Oct-2024: Corrected previously.During inspection, water proofing layer was observed. | within 6-months | Corrected
Follow Up Inspection |  | 11 | Rainforcement left exposedat top level. | For both durability and serviceability, rust proof paint or any appropriate methods is recommended. | Corrected | Oct 30 2015 | On 6-Jul-15: They have trimmed down the exposed steel. Now it is recommended that they should paint or plaster the extended portion of the steel. On 14-feb-2016: During inspection we found they have trimmed down the exposed bar and plastered the portions. On 20 April 2017: This issue was found corrected from previous inspection. On 27th Dec 2017: Corrected from previous inspection. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. No exposed rebar was found at roof level. During inspection we found they have trimmed down the exposed bar and plastered the remaining portion.. On 28-Oct-2024: Corrected previously. During inspection, no exposed rebar was found at roof. | within 6-months | Corrected
Follow Up Inspection |  | 12 | New Finding: Hairline crack on 5th floor beam and ground floor column | Involve an Engineer for checking those cracks whether it is on plaster or concrete surface. And take necessary steps accordingly. 18.01.2016 During inspection we found minor crack on 5th floor beam and ground floor column. The factory person was asked to involve an Engineer for | Corrected | Feb 17 2016 | On 14-feb-2016: During inspection we found minor crack on 5th floor beam and ground floor column. The factory person was asked to involve an Engineer for checking those cracks whether it is on plaster or concrete surface. And take necessary steps accordingly On 20 April 2017: No investigation report was found during inspection. Factory required to investigate this cracks and provide remedial measure if required. On 27th Dec 2017: Factory consultant has provided an investigation report stating that the cracks are plaster crack and not harmful for the structure. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. Factory consultant has provided an investigation report. As per investigation report the cracks were plaster crack and not harmful for the structure. During inspection no visible crack was found at beam and column. On 28-Oct-2024: Corrected previously. During inspection all crack was found repaired. | 18.01.2016 | Corrected
Follow Up Inspection |  | 13 | New Findings: On the fron side cantilever beam of ground floor roof slab is affected from loading unloading of cargo. | Involve an Engineer for checking those affected areas . And take necessary steps accordingly. | Corrected | Feb 16 2016 | On 14-feb-2016: During inspection we found that the front side cantilever beam of ground floor roof slab is affected from loading unloading of cargo. The factory person was asked to involve an Engineer for checking those affected areas. And take necessary steps accordingly On 20 April 2017: Factory provided some protection for the affected cantilever beam. But during inspection 1 nos beam found damaged. Factory required to take necessary action regarding this issue. On 27th Dec 2017: During inspection it was observed that factory management has installed barrier so that the cargo can't affect the beams also the affected beams have been repaired. Factory consultant provided a written clarification that the affected beam are ok. On 04th July 2018: Corrected from previous inspection. On 19-Sep-2021: This issue was corrected from previous inspection. During inspection it was found that factory management has installed barrier so that the cargo can't affect the beams also the affected beams have been repaired. On 28-Oct-2024: Corrected previously. Factory management has installed barrier so that the cargo can't affect the beams and the affected beams found repaired. | 18.01.2016 | Corrected

## Fire
Date
15-Mar-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Taratex Fashion Limited, 6/1, Naimuddin Mollah Road, North Augh Para, Tongi Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-08-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The elevator shaft was not separated by fire- rated construction on all floors. | Seal the elevator shaft on all floors. | Corrected on Accord 1st follow-up inspection. Update Status : Corrected | Jun 7 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. Found sealed. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. Lift core was sealed on all floors. | Within 1 month | Corrected
Initial Inspection |  | 2 | The boiler, generator and transformer rooms were not separated by fire-rated construction due to openings, non- rated doors and penetrations. The generator room was not separated from the sub station (transformer room). | Separate the boiler, generator and transformer rooms by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected | May 15 2016 | On 14/02/2016: In progress. L/C for fire doors has opened. The factory have to complete the installation within 30-Mar-16. On 12/04/2016: Fire rated doors are available in the factory. Factory ensures that fire rated door installation and civil work will be completed within 15/05/2016. On 16/08/2016: Not completed yet. On 24/10/2016: Partially corrected. Factory has installed fire doors at generator and transformer room but was keeping the doors open. Installation of magnetic door holder is still pending. Boiler and compressor rooms were not properly separated yet. On 27/12/2016: Partially Corrected. Boiler room shall be provided with Fire door. L?C has been opened for Fire Door. On 27/07/2017: Fire rated door has not been installed in electric boiler room. Window in compressor room shall be sealed. On 05/11/2017: Corrected. On 04/July/2018: Installation of fire door at the boiler room is balanced (Previously installed fire door had to unbolted due to the retrofitting work). Some unsealed penetration was observed at the utility section. On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Rooms used for combustible storage are not separated by fire- rated construction. Specifically the first floor finished goods storage room and the ground floor accessory store, wastage warehouse and warehouse. Access to the first floor northeast exit stair passes through finished goods storage room. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Provide a 1-hr fire rated exit passageway leading to the first floor northeast exit stair. The ground floor warehouse storage room is located within the the accessory store, thus separation of the accessory store is only required. | Corrected | May 15 2016 | On 14/02/2016: In progress. L/C for fire doors has opened. The factory have to complete the installation within 30-Mar-16. Location: 4th floor (Packing area) & 1st & 2nd floor ( Finishing area). On 12/04/2016: Fire rated doors are available in the factory. Factory ensures that fire rated door installation and civil work will be completed within 15/05/2016. Location: Ground floor and 1st floor. On 16/08/2016: Not completed yet. On 24/10/2016: Fire door installation work is in progress. Extended timeline from the factory is not accepted. They have to complete it within Accord given timeline. On 27/12/2016: In progress. Fire door L/C has been opened and shall be installed. On 27/07/2017: Fire rated door has not been interfaced with FACP. On 05/11/2017: Interfacing work has been completed. Need to seal some penetration. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Areas used for combustible storage, open to the factory floor, are not separated by fire-rated construction. Specifically areas on the first, second and third floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Corrected | May 15 2016 | On 14/02/2016: In progress. L/C for fire doors has opened. The factory have to complete the installation within 30-Mar-16. On 12/04/2016: Factory will limit the storage area within 30/04/2016. Factory also ensures that fire rated door installation and civil work will be completed within 15/05/2016. Location: Ground floor and 1st floor. On 16/08/2016: Not completed yet. On 24/10/2016: No action has been taken yet. Extended timeline from the factory is not accepted. They have to complete it within Accord given timeline. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Refer to issue no 29. On 27/02/2022: Refer to issue no: 29. On 21/08/2024: Refer to issue no. 29. | Within 3 months | Corrected
Initial Inspection |  | 5 | The exit stairs are not separated from work areas and other spaces on each floor by fire- rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic- closing devices tied to the fire alarm system. | Corrected | May 15 2016 | On 14/02/2016: In progress. L/C for fire doors has opened. The factory have to complete the installation within 30-Mar-16. On 12/04/2016: Fire rated doors are available in the factory. Factory ensures that fire rated door installation and civil work will be completed within 15/05/2016. On 16/08/2016: Fire door installation is not completed yet. On 24/10/2016: Fire door installation work is in progress. Office area on 1st floor is not properly separated yet. Door coordinators were found non-functional. Installation of magnetic door hold device is still pending. Extended timeline from the factory is not accepted. They have to complete it within Accord given timeline. On 27/12/2016: In progress. Magnetic hold open device shall be installed in all the Fire doors. L/C has been opened for Fire doors for office space. On 27/07/2017: Fire rated door has not been interfaced with FACP. On 05/11/2017: Interaction work is going on. On 04/July/2018: In progress On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. On 21/08/2024: Corrected. Factory shall ensure fire door components such as door closers, door coordinators are properly functional. | Within 3 months | Corrected
Initial Inspection |  | 6 | Unsealed penetrations (hydrant piping) are located in the fire-rated floor/ceiling assemblies on many of the floors. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation. | Corrected | Jun 7 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 7 | Egress doors and gates with locking features are provided at building exits, exit stairs, along egress routes and at exit discharge. All gates and doors were open and unlocked during the inspection. | Remove locking features from all egress doors and gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 11 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. No non-complaint locking features were found during the time of inspection. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Storage was located in each exit stair on various floors. | Remove all storage from exit stairs and egress paths. | Corrected on Accord 1st follow-up inspection. Update Status : Corrected | Jul 11 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 9 | Collapsible gates and sliding doors are provided at building exits, exit stairs, along egress routes and at exit discharge. | Replace all gates and sliding doors along the means of egress with side-hinged, swinging egress doors If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected on Accord 2nd follow-up inspection. Update Status : Corrected | Jul 11 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. No non-complaint gates were found during the time of inspection. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 10 | The egress doors through the main sliding doors to the main road do not swing in the direction of egress travel. | Modify the egress doors to swing in the direction of egress travel. | Corrected on Accord 2nd follow-up inspection. Update Status : Corrected | Jul 11 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. Swing direction modified. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 11 | The southwest and west exit stairs discharge inside the building to the ground floor. The west exit stairs discharge to a car port and the southwest exit stairs discharge to the interior of the building. | Modify the southwest exit stair to discharge directly outside. Provide a 2-hr fire-rated exit passageway leading directly outside for the west exit stair (vestibules to separate any storage areas). Alternately, provide sprinkler protection for discharge floor in accordance with NFPA 13. | Update Status : Corrected. Relevant all work installation is done and all kind of penetration is closed. | May 15 2016 | On 14/02/2016: In progress. L/C for fire doors has opened. The factory have to complete the installation within 30-Mar-16. On 12/04/2016: Fire rated doors are available in the factory. Factory ensures that fire rated door installation and civil work will be completed within 15/05/2016. On 16/08/2016: Not corrected yet. The west stair was not properly separated from the building interior. On 24/10/2016: No action has been taken yet. Extended timeline from the factory is not accepted. They have to complete it within Accord given timeline. On 27/12/2016: In progress. Fire Door shall be installed in the unprotected exits open to the exit discharge towards all stairs. On 27/07/2017: Found same as last follow-up inspection. On 05/11/2017: Remediation is going on. Civil construct ration has been started. On 04/July/2018: West Exit stair on ground floor level discharges inside the building & total point is not separated from the 1st floor window opening. On 02/01/2019: Corrected On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. On 21/08/2024: Corrected. | Within 6 months | Corrected
Initial Inspection |  | 12 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Update Status : Corrected. | May 30 2016 | On 16/08/2016: Design of the new addressable fire alarm system has been submitted on 10/08/2016 for Accord review. On 24/10/2016: ACCORD reviewed design was available during the time of inspection. Factory has informed that they will open L/C with 15th November 2016. Extended timeline from the factory is not accepted. They have to complete it within Accord given timeline. On 27/12/2016: In progress. No action has been taken till the last follow up. On 27/07/2017: Installation work will be started soon. On 05/11/2017: Installation work is almost completed. On 04/July/2018: Interfacing work with the fire pump & other control valves is pending On 02/01/2019: Installation work is completed. T&Cx is pending. 14-Jan-2020: Factory asked time extension till 20 Jan 2020 to submit Pre T&C documents. Time extension not accepted. Follow Accord recommended timeline. On 30/09/2020: T&CVI found that the system is not corrected. See the detailed T&CVI report. On 11/Jan/2022: T&CVI found that system is approved. See detail T&C report. On 27/02/2022: Corrected as per last T&CVI. On 21/08/2024: Corrected. 1 network trouble was found. Factory is working on troubleshooting. Factory shall always keep the FACP in normal condition. | Design within 4 months, install within 9 months | Corrected
Initial Inspection |  | 13 | The fifth floor was under construction during the inspection and thus not provided with emergency lighting, exit signs, emergency evacuation plans, fire hoses, fire alarm system components, a fire detection system, portable fire extinguishers and manual fire fighting equipment | Before occupying the fifth floor with factory operations, provide each fire and life safety system/component in accordance with its respective standard. | Corrected on 5th follow-up inspection. Update Status : Corrected | Apr 30 2016 | On 14/02/2016: No action has been taken yet. On 12/04/2016: No action has been taken yet. On 16/08/2016: Partially corrected. On 24/10/2016: Corrected. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Immediate | Corrected
Initial Inspection |  | 14 | Inspection, testing, and maintenance of the fire alarm system is not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | We have opened LC for Fire Alarm system on 22.03.2017. We will complete the installation work as per below schedule: Work Description starting Date Finished Date Design and drawing review (Done) LC. Opening (Done) Fire Alarm Equipment in-house (Done) Fire Alarm system installation Worked is going on & already 95% worked done. and Approximate finished date : (31-10-17) Update Status : Corrected | May 30 2016 | On 14/02/2016: In progress. It is an integrated part of fire alarm system. On 12/04/2016: In progress. It is an integrated part of fire alarm system. On 16/08/2016: It is an integrated part of fire alarm system. On 24/10/2016: It is an integrated part of fire alarm system. On 27/12/2016: It is an integrated part of Fire Alarm System. On 27/07/2017: It is an integrated part of fire alarm system. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 15 | Based off observations, the existing smoke detectors tied to the fire alarm were not adequately provided. | Based on ceiling configuration, provide additional detectors where needed, and space them in accordance with NFPA 72. | Update Status : Corrected. | May 30 2016 | On 14/02/2016: It is an integrated part of fire alarm system. On 12/04/2016: In progress. It is an integrated part of fire alarm system. On 16/08/2016: It is an integrated part of fire alarm system. On 24/10/2016: It is an integrated part of fire alarm system. On 27/12/2016: It is an integrated part of Fire Alarm System. On 27/07/2017: It is an integrated part of fire alarm system On 05/11/2017: It is an integrated part of fire alarm system On 04/July/2018: Integrated part of Fire Alarm & Detection System. During T&C, this issue will be evaluated accordingly. On 02/01/2019: It is an integrated part of fire alarm system. 14-Jan-2020: Factory asked time extension till 20 Jan 2020 to submit Pre T&C documents. Time extension not accepted. Follow Accord recommended timeline. On 30/09/2020: T&CVI found that the system is not corrected. See the detailed T&CVI report. (RCH) 18-Nov-2020: Pre-T&C Documents is under review. On 11/Jan/2022: T&CVI found that system is approved. See detail T&C report. On 27/02/2022: Corrected as per last T&CVI. On 21/08/2024: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 16 | Some battery powered emergency lighting units did not function in test mode (burned out, broken, etc.). | Reguarly test the emergency lighting system on each floor and replace/repair lights as needed. | Corrected on 4th follow-up inspection. Update Status : Corrected | Aug 16 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. Found functional during the testing. On 27/12/2016: Corrected. On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Within 1 month | Corrected
Initial Inspection |  | 17 | Inspection, testing, and maintenance for the emergency lighting system was not in accordance with The ACCORD standard. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected on 5th follow-up inspection. Update Status : Corrected | Apr 30 2016 | On 14/02/2016: In progress. On 12/04/2016: In progress. Inspection, testing, and maintenance record for the emergency lighting system will be conducted according to ACCORD standard within 30/04/2016. On 16/08/2016: ITM record was found but not inspected as per Accord standard. Also some exit sign was not illuminated. On 24/10/2016: Corrected. Factory is maintaining a standard checklist as per code. On 27/12/2016: Corrected. On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. Factory shall update the emergency light checklist. | Within 3 months | Corrected
Initial Inspection |  | 18 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along all egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected on 4th follow-up inspection. Update Status : Corrected | Apr 30 2016 | On 14/02/2016: In progress. On 12/04/2016: In progress. Factory has installed emergency light but, the installed emergency lights do not provide adequate illumination level. On 16/08/2016: Corrected. On 24/10/2016: Corrected as per actual site. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. On 21/08/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 19 | New Finding: The existing factory building with an occupiable floor greater than 10 m (33 ft) above the finished grade and they have standpipe system but the existing standpipe system was not comply with the | Modify or install the standpipe system throughout the building in accordance with NFPA 14 and design shall be submited to Accord for review. | Already corrected | Jul 30 2016 | On 24/10/2016: ACCORD reviewed design was available during the time of inspection. Factory has opened L/C and has informed that they will finish the work as quickly as possible. On 27/12/2016: In progress. Fire Pump is inhouse. Installation shall be started soon. On 27/07/2017: Installation work is going on. On 05/11/2017: Installation work has been completed. Pump suction is negative. On 04/July/2018: Factory management has ensured the positive suction for installed fire pump. Interfacing with FACP shall have to be completed. Proper separation of fire pump room from the exit stair shall have to be ensured. On 02/01/2019: Installation work is completed. T&Cx is pending. 5-Jan-2020: Time extension till January, 2020 not accepted. Follow Accord recommended timeline. On 30/09/2020: T&CVI found that the system is not corrected. See the detailed T&CVI report. (RCH) 18-Nov-2020: Pre-T&C Documents is under review. (RCH) 14-Dec-2020: Pre-T&C Documents is under review. On 11/Jan/2022: T&CVI found that system is approved. See detail T&C report. On 27/02/2022: Corrected as per last T&CVI. On 21/08/2024: Corrected. Fire pump was functional. | 2 Months for design review and 6 Months for modification or newly installation. | Corrected
Follow Up Inspection |  | 20 | New Finding: Manual on-off switch is provided for emergency exit lights in all floors | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected on Accord 2nd follow-up Inspection Update Status : Corrected | Jul 11 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. Not found. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 21 | New Finding: Both side handrails are not provided in the South-East exit stairs. | Provide both side handrails on the South-East exit stair having a minimum height 34 inch. | Corrected on Accord 2nd follow-up Inspection Update Status : Corrected | Aug 1 2015 | On 14/02/2016: Corrected. On 12/04/2016: Corrected On 16/08/2016: Corrected. On 24/10/2016: Corrected. Handrail provided. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | 3 months | Corrected
Follow Up Inspection |  | 22 | New finding (2nd follow up): The width of egress aisles is less than 36-inch. Location: 3rd & 4th floor. | Provide minimum aisle widths of 36-inch | Corrected on 3rd followup inspection. Update Status : Corrected | Mar 14 2016 | On 14/02/2016: New Finding On 12/04/2016: Corrected On 16/08/2016: Corrected. On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 23 | New finding in 5th Follow-up: Storage was located in the egress path | Keep egress path and stair clear of storage. | Corrected | Nov 11 2016 | New Finding On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 24 | New finding in 5th Follow-up: Storage was located under the exit stair. Location: at the roof as well as under all the exit stairs. | Remove storage from the exit stairs and egress path | Update Status : Corrected. | Nov 11 2016 | New Finding On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Reopened. Storage and obstruction observed on the egress path. On 27/02/2022: Corrected. On 21/08/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 25 | New finding in 5th Follow-up: The width of egress aisles is less than 36-inch. | Provide minimum aisle widths of 36-inch and keep the aisle free from any obstacle. | Corrected | Dec 15 2016 | On 27/12/2016: Corrected On 27/07/2017: Corrected. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected. On 27/02/2022: Corrected. On 21/08/2024: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 26 | New finding in 5th Follow-up: Loading/unloading and car parking area is not properly separated from other occupancy. | Provide a minimum 2 hour fire rated construction to separate the area from other occupancy. | Corrected | Dec 15 2016 | On 27/12/2016: Corrected. No storage can be kept in the loading unloading area even for temporary purpose. On 27/07/2017: Corrected as per last follow-up inspection. On 05/11/2017: Corrected. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. On 21/08/2024: Corrected. | 1 month | Corrected
Follow Up Inspection |  | 27 | New finding (7th follow-up): Dining area is not separated from other occupancies with fire rated assemblies | Re-locate the dining area or separate the dining area from other occupancies with fire rated construction | Update Status : Corrected. | Aug 27 2017 | On 27/07/2017: New finding. On 05/11/2017: Installation work is going on. On 04/July/2018: Corrected On 02/01/2019: Corrected. On 30/09/2020: Reopened. Not seperated from other occupencies. On 27/02/2022: Corrected as per site condition. On 21/08/2024: Corrected. | With in 1 month | Corrected
Follow Up Inspection |  | 28 | New Finding (10th follow up): Fire pump room is not seperated | Separate the fire pump room from other occupancies with 2 hr. fire rated construction | Update Status : Fire door installation completed. | Feb 2 2019 | On 02/01/2019: New finding. On 30/09/2020: Corrected On 27/02/2022: Corrected as per previous follow-up. Note: Fire pump room discharge found through fabric inspection area at Ground floor. Fire pump rooms not directly accessible from the outside shall be accessible through an enclosed passageway from an enclosed stairway or exterior exit as per NFPA 20. On 21/08/2024: Corrected. | With in 1 month | Corrected
Follow Up Inspection |  | 29 | New Finding (11th follow up): Areas used for combustible storage, open to the factory floor, are not separated by fire-rated construction on the fifth and first floors. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Update Status : Corrected. | Oct 30 2020 | On 30/09/2020: New finding. On 27/02/2022: Corrected. In-process storage area was found within limit. On 21/08/2024: Corrected. In-process storage was found within limit. However, exxcessive storage was located under the cutting tables which must be removed. | 1 month | Corrected

## Electrical
Date
15-Mar-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Taratex Fashion Limited, 6/1, Naimuddin Mollah Road, North Augh Para, Tongi Gazipur, Gazipur, Dhaka
Date of Inspection |  | 2014-08-06
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | As-build electrical Single Line Diagram (SLD) is not correct while, wiring layout design drawing is not prepared. | The factory must have corrected as-build electrical SLD with electrical wiring layout designs and drawings. Any changes in load, protection system, conductors, generation and supply system must be reflected in the as-build SLD and drawings. | Corrected | May 15 2016 | On 14/02/2016: Not corrected: This issue is not closed yet. The drawing was submitted and revert back with some observations. New committed timeline is given till March 06, 2016. On 12/04/2016: This issue is not corrected yet. New committed timeline has given till 15/05/2016. On 16/08/2016: Not Corrected. Provide permanent marking of panel board and identification for circuit as per SLD. On 24/10/2016: Still not corrected. On 27/12/2016: Not Corrected. On 27/12/2016: Not Corrected. On 05/11/2017: Not Corrected. On 04/07/2018: Corrected. | 10 WEEKS | Corrected
Initial Inspection |  | 2 | Thermo graphic scanning of the entire electrical system has not been performed. | Thermo graphic scanning of the entire electrical system must be performed on tri-annual basis and recorded. | Corrected | Dec 23 2015 | On 14/02/2016: Last thermo graphic inspection was done on February 10, 2016. Next thermo graphic inspection will be due on August 2016. | 10 WEEKS | Corrected
Initial Inspection |  | 3 | Electric safety program is not initiated. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | May 15 2016 | On 14/02/2016: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 4 | 11KV UG power cable partially laid on floor inside control room. | Underground power cable should be protected adequately in cable duct to full length. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 24 WEEKS | Corrected
Initial Inspection |  | 5 | No cable sleeve provided at the entry of 11KV UG power cable inside the electrical room. Cable not protected. | Cables must be drawn through cable sleeve at the wall crossing and the remaining opening must be sealed with fire rated material. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 6 | Oil cup below transformer breather is empty. | Breather oil cup must be filled with transformer oil to required level as instructed by the manufacturer. | Corrected on Accord 1st follow-up Inspection. | Nov 8 2015 | On 14/02/2016: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 7 | Oil level in transformer conservator tank is below the minimum requirement. | Transformer oil must be filled to the required level after shutdown. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 2 WEEKS | Corrected
Initial Inspection |  | 8 | Oil leakage from the transformer. | Leakage must be identified during maintenance and repaired it as soon as possible. Preferably, Assign supplier company to take necessary steps as soon as possible | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 1 WEEK | Corrected
Initial Inspection |  | 9 | The leakage current collector of HT power cable is connected to the transformer body. | Leakage current collector of HT power cable should be grounded individually. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEK | Corrected
Initial Inspection |  | 10 | Transformer body connected to only one earth. The earth wire connected to transformer body is not as per standard size. | Transformer body should be provided with two earth connection and should be done with solid Cu/GI wire or strip. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 12 WEEK | Corrected
Initial Inspection |  | 11 | Earth cable terminating at earth bar without lugs. | Provide appropriate size cable thimble/lugs for terminating the cable at the earth bar | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 12 | Rubber mat not provided inside the transformer room. | Adequate rubber mat should be provided inside the transformer room and inside the control panel room. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 13 | Panel doors not connected with earth bond. | Panel door(s) must be connected with earth bond connecting frame and door. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 2 WEEKS | Corrected
Initial Inspection |  | 14 | Panels are installed directly on concrete floor without base/plinth. No adequate space between floor and earth bar. | Panels must be mounted with base/plinth on the concrete floor. To avoid live parts coming in contact with water and easy operation and maintenance. (Base / Plinth can be supplied by the manufacture). | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 24 WEEKS | Corrected
Initial Inspection |  | 15 | Barrier/separators between different phases are not installed. | Install separators between different phases of MCCB. Standard separators provided by the MCCB manufacturer must be used. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 16 | Panel base plate removed to allow entry and exit of cables. | Make circular hole at the base plate and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable glands | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Oct 31 2015 | On 14/02/2016: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 17 | Opening on wall for cable tray left open | All openings on wall made for cable route must be sealed adequately with non-combustible material. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Dec 31 2015 | On 14/02/2016: Corrected. Proper duct has been provided. | 24 WEEKS | Corrected
Initial Inspection |  | 18 | PVC surface conduits are not supported adequately on wall. | Surface conduit must be supported adequately by clamp/saddle at regular interval. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Dec 31 2015 | On 14/02/2016: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 19 | PVC flexible conduit used in boiler room. Flexible conduit hanging and not protected. | Steel flexible/spiral conduit should be use in boiler room. The conduit must be supported adequately or use rigid conduit for cable protections. | Corrected on Accord 1st follow-up Inspection. | Apr 30 2016 | On 06/07/2015: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 20 | Wires exposed while transiting from concealed wiring to surface conduit wiring (Typical) | Provide circular junction box at the transitional point. Wires must be protected throughout the entire length in a wiring system. | Corrected on Accord 3rd follow-up inspection | Dec 3 2016 | On 14/02/2016: Corrected. | 12 WEEKS | Corrected
Initial Inspection |  | 21 | Spacing around the MCCBs narrow and crowded inside panel. | Check and assess the distribution system. Additional panel may be installed to reduce cable load in the existing panel. | Corrected on Accord 3rd follow-up inspection | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 22 | Wires are exposed from concealed wiring (Typical). | Conduit must be provided to full length of wiring. Use appropriate conduit at the surface to protect the wires. | Corrected on Accord 3rd follow-up inspection | Dec 3 2016 | On 14/02/2016: Not corrected. This issue is not closed yet as wires for many fittings are exposed and kept hanging. New committed timeline is given till March 20, 2016. On 12/04/2016: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 23 | Deposit of lint and dust on the surface of MCCB and cable inside the distribution panel. | Clean inside panels periodically. Electrical installations should be free from lint and dust. All panels must be vermin proof. | Corrected on Accord 1st follow-up Inspection. | Jun 7 2015 | On 06/07/2015: Corrected. | Immediately | Corrected
Initial Inspection |  | 24 | MS wiring dust below work bench not covered at ends. Excess deposit of lint inside wiring ducts. | Wiring duct must be closed from all ends to prevent ingression of lint and dust. Clean the ducts regularly as normal operation and maintenance. | Corrected on Accord 1st follow-up visit. | Jun 7 2015 | On 06/07/2015: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 25 | Aluminum channel is open from top and end cover not provided. Wiring duct has deposit of lint and dust. | Wiring duct must be covered from top and ends should be sealed to prevent the ingression of lint and dust. Clean the wiring duct regularly. | Corrected on Accord 3rd follow-up inspection | May 15 2016 | On 14/02/2016: Not corrected: This issue is not closed yet as the work is not completed yet. Work is in progress. Still few floors are in progress. New committed timeline is given till March 20, 2016. On 12/04/2016: Corrected. | 8WEEKS | Corrected
Initial Inspection |  | 26 | Wire/cable joints in wiring systems are not properly done and not protected adequately. Insulation done with plastic tape. | Wires/cable must be terminated at terminals or use appropriate jointing. PIB tape and heat- shrink tubes may be used for insulation. | Corrected on Accord 1st follow-up visit. | Jun 7 2015 | On 06/07/2015: Corrected. | 4 WEEKS | Corrected
Initial Inspection |  | 27 | Ceiling fan connection done without ceiling rose. | Ceiling fan and ceiling fittings should be connected from ceiling rose. | Corrected on Accord 1st follow-up visit. | Jun 7 2015 | On 06/07/2015: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 28 | Deposit of lint and dust inside the power socket box. | Power socket must be installed properly to prevent ingression of lint and dust. Clean the box and check frequently. | Corrected on Accord 3rd follow-up inspection | Feb 28 2016 | On 14/02/2016: Not corrected: This issue is not closed yet as the work is not completed yet. Work is in progress to seal the opening of the socket box. New committed timeline is given till March 20, 2016. On 12/04/2016: Corrected. | 4WEEKS | Corrected
Initial Inspection |  | 29 | Cables are exposed from the floor while transiting from surface conduit to concealed under floor (Typical). | Provide cable protections at the base of the wall. Cable must be protected to full length. | Corrected on Accord 1st follow-up visit. | Jun 7 2015 | On 06/07/2015: Corrected. | 8 WEEKS | Corrected
Initial Inspection |  | 30 | Inconsistency between the reading and rating of MCCB installed. | Measurement should be taken during the peak load time and accordingly replace high current rated MCCB with appropriate one. | Corrected | May 15 2016 | On 14/02/2016: This issue is not closed yet as over-sized circuit breakers are available. New committed timeline is given till March 20, 2016. On 12/04/2016: This issue is not corrected yet. New committed timeline has given till 15/05/2016. On 16/08/2016: Not Corrected. On 24/10/2016: Still not corrected. On 27/12/2016: Corrected | 8 WEEKS | Corrected
Initial Inspection |  | 31 | Surface wiring in PVC flexible conduit not supported adequately. | Surface conduit should be supported adequately at regular interval with clamp/saddle. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Dec 31 2015 | On 14/02/2016: Corrected. | 8 WEEKS | Corrected
Follow Up Inspection |  | 32 | New Finding: Earth busbar size is inadequate/undersize in panel. | Used adequate earth busbar to be rated to safely conduct the maximum fault current of phase to ground fault with negligible voltage drop. | Corrected on Accord 3rd follow-up inspection | Mar 20 2016 | On 14/02/2016: Partially corrected. This issue is not closed yet as the earth continuity conductor is inadequate. However, the bus bar size has been increased adequately. Work is in progress. Still few floors are in progress. New committed timeline is given till March 31, 2016. On 12/04/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 33 | New Finding: Battery terminals are left open. | Use insulated rubber cap to cover all the battery terminals | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Sep 25 2015 | On 14/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Power cable is buried in the concrete floor. | Construct a cable trench for distributing power cables. Then cover it by checkered plate. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Dec 31 2015 | On 14/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Transformer Oil Test report is unavailable. | Check the transformer oil condition by performing oil test. Do it once in a year and keep the record. | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Jun 2 2016 | On 14/02/2016: Last transformer oil test was done on February, 2016. Next transformer oil test will be due on February, 2017. | 2 Months | Corrected
Follow Up Inspection |  | 36 | New Finding: Maintenance records do not detail out all the electrical equipment/machinery. | Maintenance Manager or Safety Officer must keep accurate records and ensure that they reflect actual factory day to day operations | Corrected on 2nd follow-up Inspection on 14 Feb-2016 | Sep 25 2015 | On 14/02/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Heat sources (choke/ballast of tube lights) are installed inside the cable channel which is kept open. | Need to relocate the heat sources (chokes or ballasts) from the cable channel and the cable duct needs to be covered. | Corrected | May 15 2016 | On 14/02/2016: New extended timeline from 4/20/2016 to 4/30/2016. On 12/04/2016: This issue is not corrected yet. New committed timeline has given till 15/05/2016. On 16/08/2016: Not Corrected. They are replacing tube light with LED light. On 24/10/2016: Still not corrected. On 27/12/2016: Corrected. Most of the lights are replaced with LED lights and rest of the ballasts are removed from cable channel | 2 Months | Corrected
Follow Up Inspection |  | 38 | New Finding: Panel/Distribution boxes are not readily accessible. | Take necessary initiative thus every panel/distribution board can be easily accessible | Corrected on Accord 3rd follow-up inspection | Mar 20 2016 | On 12/04/2016: Corrected. | 4 weeks | Corrected
Follow Up Inspection |  | 39 | New Finding: Light in store room / storage areas is uncovered. | Lights in store room / storage areas shall be covered. | Corrected on 4th follow-up inspection. | May 15 2016 | On 12/04/2016: This issue is corrected partially. New committed timeline has given 15/05/2016 On 16/08/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Lightning Protection System(LPS) has not installed yet | Design and Install LPS for your factory as per standard. | Corrected | Jul 31 2016 | On 16/08/2016: Not Corrected. Design needs little modifications. Installation is pending. On 24/10/2016: Still not corrected. Installation has been started. On 27/12/2016: Not Corrected. 95% installation are ok but class II conductor should go directly to pit. On 27/07/2017: Corrected | 15/06/2016 | Corrected
Follow Up Inspection |  | 41 | New Finding: Excess cables coiled and kept at the back of panel. | Rearrange cables using cable tray/ladder; or trim the unnecessary cables and use only the required length (If it is HT cable, do not trim it rather rearranging it). | Corrected on 4th follow-up inspection. | Jun 15 2016 | On 16/08/2016: Corrected. | 15/06/2016 | Corrected
Follow Up Inspection |  | 42 | New Finding: Hot spots at terminations inside panel. | Identify the overloading, loose connection, unbalanced load which may cause the excessive heat rise and take action accordingly. However, immediately correct such point. | Corrected on 5th follow-up inspection. | Apr 25 2016 | On 16/08/2016: Not Corrected. Address the hot spot immediately and thermo graphic scanning report date is expired. Complete the scanning of whole electrical system after every 6 month On 24/10/2016: Corrected. Hot spots have been removed. | 1 Week | Corrected
Follow Up Inspection |  | 43 | New Finding: Power cables are bent excessively | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Corrected on 5th follow-up inspection. | Oct 20 2016 | On 24/10/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per cable current ampacity/load current; if adjustment is not possible, replacement will be the only way. | we have already replaced the cable & waiting for Accord verification. | Sep 10 2017 | On 05/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Distribution boards have no clear identification markings. | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. | We have already completed this work. | Sep 10 2017 | On 05/11/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Field information has no/less reflection in existing SLD. | Draw as built electrical SLD mentioning all required information by qualified engineer and get it reviewed by RSC. Electrical SLD must be updated properly when electrical system is modified. | SLD Implementation work is going on and within short of time the issue will be closed. | Feb 13 2024 | On 21-Aug-2024: Not Corrected. Factory submitted SLD to RSC on 18-Aug-2024 which is under review. RPO Comments On 08-May-2025 The factory management is required to implement in the field as per the accepted SLD with immediate concern. On 19/06/2025 (Special Inspection): Not Verified. This issue is not under inspection scope. | 2 Months | In Progress
Follow Up Inspection |  | 47 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Adequate space [ 42'' ] is ensured at the conservator tank side. | Jan 8 2024 | On 21-Aug-2024: Not Corrected. Adequate space is not available at 2 sides. Factory needs to relocate wall at conservator tank side to ensure adequate space. RPO Comments On 27-OCT-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 19/06/2025 (Special Inspection): Not Verified. This issue is not under inspection scope. | 1 Month | In Progress
Follow Up Inspection |  | 48 | New Finding: Hot spots have been observed at some points. (above 40ºC of ambient) | Hot spots must be eliminated from entire electrical system. | We have taken few initives to keep Temperature control within limit. 1. We have changes few breaker 2. Load distribution changes from one DB to another DB 3. Installed Exhaust fan inside every DB board 4. Breaker joining place cleaned 5. Update thermal report attached. | Sep 5 2024 | RPO Comments On 27-OCT-2024: The factory management reported the remediation completion. This item will be verified in the next inspection. On 19/06/2025 (Special Inspection): Corrected. They have changed breakers and cables of different DBs of the factory. During inspection, no hot spot and critial temperature observed. | 2 WEEKS | Corrected