## Structural
Date
03-Nov-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED, South Gouripur, Dhaka
Date of Inspection |  | 2016-05-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Preliminary column FoS calculated values of 2 storied steel shed and 4 storied RCC building based on as-built configuration confirmed via structural drawings have been found adequate. 3 storied RCC building has been found inadequate. | Some doubts about safety; Concrete strength shall be confirmed by core cutting. Under guidance from a qualified structural engineer arrange Detail Engineering Assessment of the structure. | Management contact a qualified structural engineer organization for Detailed Engineering Assessment (DEA) of the structure. DEA already submitted to Alliance waiting for Approval. | Jan 4 2017 | On 14/02/2018: DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. Moreover, core cutting layout and original core test reports were available but core cutting location could not be verified due to finishes and paints. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance. On 30th April 2019: This issue has been covered in DEA which has been re-accepted from Alliance on 4th Nov 2018. Factory has completed all remediation works as per accepted drawing in Two storied steel shed and single storey steel shed. Retrofitting certificate has also been provided by the factory consultant. On 02-Sep-2024: Corrected previously. DEA was re-accepted from ALLIANCE on 04-Nov-2018. Factory has completed all the retrofitting works of single storied shed and two storied shed as per accepted retrofitting drawings. During inspection, retrofitting completion certificate was available. The 3 storied RC building is no more being used by the factory. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 2 | No testing was done for assessment of the strength of the concrete. FoS have been found less than 1.86 in 3 storied RCC building. | Concrete strength shall be confirmed by core cutting in 3 storied RCC building. | DEA already submitted to Alliance waiting for Approval. | Jan 4 2017 | On 14/02/2018: Core cutting layout and original core test reports were available but core cutting location could not be verified due to finishes and paints. On 20/09/2018: Core cutting location has been verified by on-site corroboration and credible pictorial evidence. On 30th April 2019: Corrected from previous inspection. On 02-Sep-2024: Corrected previously. The 3 storied RCC building is no more being used by the factory. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 3 | 1) 1 storied steel shed: Credible structural design documents are available for review and kept on site. 2) 2 storied steel shed: Credible structural design documents are available for review and kept on site. 3) 4 storied RCC building (Office, Child care, Medical, Sample & Fire control room): Credible structural design documents are available for review and kept on site. There is a Self supported stair but design documents are not available. 4) 3 storied RCC building (Canteen, Accessories store, Fabrics store & Maintenance): Structural design documents are available but do not match with existing structure and therefore shall be consider not credible. 5) Utility Area (Boiler, Compressor, Substation and Transformer): Undocumented structure. 6) Generator room: Undocumented structure. 7) Proposed pump house: Undocumented structure. | A qualified structural engineer shall be engaged to prepare credible as-built documents for 3 Storied building; Utility Area (Boiler, Compressor, Substation and Transformer); Generator room and Proposed pump house based on the requirements of Part 8 Section 8.19 of the Alliance Standard. | DEA already submitted to Alliance waiting for Approval. | Jan 4 2017 | On 14/02/2018: As-built drawings are prepared as a part of DEA. DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance. On 30th April 2019: As built drawing has been produced and re-accepted as a part of DEA. During inspection as-built drawing was generally matched with as-built condition. On 02-Sep-2024: Corrected previously. On 16-Oct-2025: Previously corrected. However, during the inspection, a mismatch was identified in the retrofitting implementation (bracing) of the one-storied steel shed. Later, the factory installed bracings as per the accepted drawings and submitted pictorial evidence, which was found satisfactory. | Aug 15 2016 | Corrected
Initial Inspection |  | 4 | Signs of standing water have been noticed over roof of 3 storied RCC building and utility building. Corrosion has been noticed in north-east side structural steel column of 1 storied steel shed. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Already Management corrected by maintenance of the identified issues all areas of needed. | Jul 2 2016 | On 14/02/2018: Factory has no operation in 3-storied building. Currently the building is occupied by land owner. During inspection, corrosion found in steel beam at North of Shed-2. No corrosion has been found at shed-1. On the other hand, no remedial plan was found in the time of inspection. On 20/09/2018: Corrosion has been repaired. During the inspection, no corrosion was found at shed-2. On 30th April 2019: During inspection it was observed that 3 storey building is not building used under this factory. Factory has provide rust proof paint to protect corrosion. On 02-Sep-2024: Corrected previously. The 3 storied RC building is no more being used by the factory. During inspection, no corrosion was found in 1 storied Steel Shed. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 5 | 4 storied RCC building roof has been found without protective coating. | Provide a protective coating at the structural elements constructed with MCAC exposed to rainfall or other sources of water. Have protective coating approved by the Alliance or a qualified structural engineer. | Already Management corrected by maintenance a sealed with a protective coating to prevent water intrusion rainfall or other sources of water. | Jul 2 2016 | On 14/02/2018: Protective coating has been applied on roof. On 20/09/2018: Corrected in previous inspection. On 30th April 2019: Corrected from previous inspection. Water proofing has been provided on roof slab. On 02-Sep-2024: Corrected previously. Factory has applied water proofing layer on roof. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 6 | 1- Plastic water tank has been found over 3 storied building. 2- Plastic water tanks have been found over 4 storied building. | A qualified structural engineer shall be engage to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Already Management has taken the necessary action as per instruction of 1st RVV inspector of Building. | Nov 1 2016 | On 14/02/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance. On 30th April 2019: During inspection it was observed that 3 storey building is not building used under this factory. This issue has been covered in DEA which has been re-accepted from Alliance on 4th Nov 2018. Remediation is not required in 4 storied building. On 02-Sep-2024: Corrected previously. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 7 | Corrosion has been noticed in north-east side structural steel column of 1 storied steel shed. | Complete further testing on areas of deterioration and have a qualified structural engineer develop a remediation plan. | DEA already submitted to Alliance waiting for Approval. | Jan 4 2017 | On 14/02/2018: During inspection, corrosion found in steel beam at North of Shed-2. No corrosion has been found at shed-1. On the other hand, no remedial plan was found in the time of inspection. On 20/09/2018: Corrosion has been repaired. During the inspection, no corrosion was found at shed-2. On 30th April 2019: Corrected from previous inspection. On 02-Sep-2024: Corrected previously. During inspection, no corrosion was found at 1 storied steel shed. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 8 | Hanger bar used for running electric cables of production shed and plastic tank over roof of 4 storied RCC building and 3 storied RCC building have not been anchored and braced adequately to resist earthquake force. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Already Management has taken the necessary action adequately anchor and brace all non-structural elements to resist earthquake forces. | Jul 2 2016 | On 14/02/2018: Racks are found anchored and water tanks are found braced. On 20/09/2018: Corrected in previous inspection. On 30th April 2019: Corrected from previous inspection. Factory has sifted all racks to another building. On 02-Sep-2024: Corrected previously. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 9 | There is no such program in place (floor and roof) ensuring that the live loads for which a floor or roof is or has been designed will not be exceeded. | Develop a program to ensure that all live loads for which a floor or roof has been designed for will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Already Management developed a program to ensure that all live loads not exceeded. Factory designated Load Manager oversee this program and ensure it is enforced. | Jul 2 2016 | On 14/02/2018: Newly appointed load manager is maintaining a load register book. Also, load limit information has been provided on storage areas. During inspection, load plan was posted on suspended floor and floor loading was below the allowable limit. On 20/09/2018: Corrected in the previous inspection. A load register book has been maintained by the load manager. On 30th April 2019: Corrected from previous inspection. During inspection accepted load plan was found posted at every floor and load was found below the allowable limit (42 psf in 4 storey building and 63 psf in two storey steel building). On 02-Sep-2024: Corrected previously. During inspection, load plan was found posted in each floor of 4 storied building & 2 storied steel shed and loading was found within the allowable limit (42 psf in 4 storied building and 63 psf in 2 storied steel shed) of accepted load plan. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 10 | No designated factory load manager was noted during the assessment. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | The factory management already appointed a designated load manager. He is responsible for ensure the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. Management will be trained t | May 31 2017 | On 14/02/2018: A load manager has been appointed. On 20/09/2018: Corrected in the previous inspection. Load manager has been appointed. On 30th April 2019: Corrected from previous inspection. Load manager has been appointed and he was present during inspection. On 02-Sep-2024: Corrected previously. During inspection, load manager was present. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 11 | Load plans have not been prepared, documenting the actual maximum operational loading. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3. | Factory Management has completed load calculation by a qualified structural engineer organization. The load plans have been prepared for each floor documenting the actual maximum operational loading that is intended and /or allowable on each floor. | Jul 2 2016 | On 14/02/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. Previously accepted load plan was posted on suspended floor and floor loading was below the allowable limit. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance. Factory is required to maintain revised load plan after getting re-acceptance from Alliance. However, during inspection floor loading was within 42 psf. On 30th April 2019: Load plan has been produced and re-accepted as a part of DEA from Alliance on 4th Nov 2018. On 02-Sep-2024: Corrected previously. Load plan has been prepared as part of DEA which was re-accepted from ALLIANCE on 04-Nov-2018. During inspection, load plan was found posted in each floor of 4 storied building & 2 storied steel shed and loading was found within the allowable limit (42 psf in 4 storied building and 63 psf in 2 storied steel shed) of accepted load plan. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 12 | Load plans have not been prepared. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. Floor load plans should be visibly posted on all levels of all buildings. | Floor load plans have visibly posted on all levels of all buildings. | Jul 2 2016 | On 14/02/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. Previously accepted load plan was posted on suspended floor and floor loading was below the allowable limit. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance. Factory is required to maintain revised load plan after getting re-acceptance from Alliance. However, during inspection floor loading was within 42 psf. On 30th April 2019: Load plan has been produced and re-accepted as a part of DEA from Alliance on 4th Nov 2018. During inspection accepted load plan was found posted at every floor and load was found below the allowable limit (42 psf in 4 storey building and 63 psf in two storey steel building). On 02-Sep-2024: Corrected previously. Load plan has been prepared as part of DEA which was re-accepted from ALLIANCE on 04-Nov-2018. During inspection, load plan was found posted in each floor of 4 storied building & 2 storied steel shed and loading was found within the allowable limit (42 psf in 4 storied building and 63 psf in 2 storied steel shed) of accepted load plan. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 13 | Areas used for storage of work materials and work products have not been marked indicating the acceptable loading limits. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Prepar load plan and maintain according to allowable load. | Jul 2 2016 | On 14/02/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance on 09 May 2017. During inspection some discrepancies were found in as-built drawings. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. Signage and load limit information has been provided on storage area as per previously accepted load plan. Factory shall update the signage and load limit information as per revised load plan after getting re-acceptance form Alliance. On 20/09/2018: Factory revised the as-built drawings as per discrepancy report, but till the date of inspection, they didn't submit the revised document to Alliance Signage and load limit information has been provided on storage area as per previously accepted load plan. Factory shall update the signage and load limit information as per revised load plan after getting re-acceptance form Alliance. On 30th April 2019: During inspection load marking was found at all storage areas and load was found below the allowable limit (42 psf in 4 storey building and 63 psf in two storey steel building). On 02-Sep-2024: Corrected previously. During inspection, height restriction mark was found in storage area of 4 storied building and 2 storied steel shed. Also loading was found within allowable limit (42 psf in 4 storied building and 63 psf in 2 storied steel shed) of accepted load plan. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 14 | Certificate of Occupancy was not available for review. | Certificate of occupancy shall be obtained from appropriate authority. | The factory management already applied to PWD for Occupancy Certificate on 13/02/2017. | Apr 30 2017 | On 14/02/2018: Not Applicable as per Alliance report. On 20/09/2018: Corrected in previous inspection. On 30th April 2019: Corrected from previous inspection. On 02-Sep-2024: Corrected previously. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected
Initial Inspection |  | 15 | All buildings except 1 storied steel shed have been found free of active signs of water intrusion due to lack of performance of the façade system. | Repair the exterior façade system to prevent water intrusion. | The Building is free of active sign of water intrusion or pounding due to lack of performance of the façade system. | Jul 2 2016 | On 14/02/2018: Exterior façade of toilet block (adjacent with shed-1) has been repaired. But during inspection, sign of water intrusion has been found inside toilet areas. On 20/09/2018: Exterior façade of toilet block (adjacent with shed-1) has been repaired. During inspection, No sign of water intrusion was found. On 30th April 2019: Corrected from previous inspection. On 02-Sep-2024: Corrected previously. During inspection, no water intrusion was found. On 16-Oct-2025: Previously corrected. | Aug 15 2016 | Corrected

## Fire
Date
03-Nov-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED, South Gouripur, Dhaka
Date of Inspection |  | 2016-05-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The exterior stairs of the Canteen & Storage Building (Stair-1 & -2) connect grade level through level 3. The exterior stair of the Office Building (Stair-2) are not separated from the buildings with the required rating due to window openings. These stairs are also not separated from the adjacent Main Factory Building-1 without having required rating of its exterior walls, as well as, required separation distances from the stairs. | Provide a fire-resistive rated assembly between the exterior exit stairs (and 10 ft beyond the ends of the stairs) and the building to achieve the required separation. Enclose any openings (windows, etc.) with required fire rated construction within that 10 ft wall section. The rated assembly should be designed and/or approved by a qualified fire protection engineer. | The building owner claim to us for his personal purposes use this build, on based that we are amendment our deed & changed layout plan, fire liancese. Also we updated Alliance accordingly. Now we are not use that building. we are waiting for RSC T&CVI. | Dec 6 2016 | On 17.10.2017: In progress. At some locations, proper fire rated separation is still pending. Factory management needs to provide proper fire separation by fire rated construction and fire rated door. On 30/04/2019: Interfacing work of fire rated door is not working properly. On 15-03-2021: Corrected. During inspection interfacing was functional. On 14/02/2022: Corrected. On 13-05-2024: Corrected. | Dec 14 2016 | Corrected
Initial Inspection |  | 2 | Interior exit stair-1 of the Office Building and 3 exit stairways of Main Factory Building-2 do not terminate at an exit discharge, they terminate to the interior of the buildings on the ground floor. | Exits shall discharge directly to the exterior of the building unless meeting the requirements of Alliance Standard Section 6.17.2 or 6.17.3. If requirements are not met, route exits directly to the exterior or provide an exit passageway in accordance with Alliance Standard Section 6.15 for non-compliant arrangements. Consult a qualified fire protection engineer to design and/or approve the required exit passageway. | Interior exit stair-1 of the Office Building is separated with rated fire barrier. we are waiting for RSC T&CVI. | Sep 13 2016 | On 17.10.2017: In progress. Factory management has constructed fire rated wall and installed fire rated door and interfaced with FACP, only T&C is balanced. On 30/04/2019: Interfacing work of fire rated door is not working properly. On 15-03-2021: Corrected. During inspection interfacing was functional. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 3 | Exit discharge of the stairs of Main Factory Building-2 is to the interior of the production floor. Exit discharge of the Canteen & Storage Building reenters Main Factory Building-1. | Exit discharge shall not reenter other buildings. Route exits directly to the exterior or provide an exit passageway in accordance with Alliance Standard Section 6.15 or an Egress Court in accordance with Alliance Standard Section 6.17.2 for non-compliant arrangements. Consult a qualified fire protection engineer to design and/or approve the required exit passageway or egress court. | Exit discharge route exits directly to the exterior. Management designed the required exit passageway and implemented egress.We are waiting for RSC T&CVI. | Sep 18 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: In progress. Factory management has constructed fire rated wall and installed fire rated door and interfaced with FACP, only T&C is balanced. On 30/04/2019: Interfacing work of fire rated door is not working properly. On 15-03-2021: Corrected. During inspection interfacing was functional. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 4 | The fire command room is housed on the ground floor of the Office Building, It was noticed that the alarm notification was indicated on the fire alarm control panel during a test run of the system. | Have the system inspected and/or repaired by a qualified fire alarm installation company. | Trouble or alarm notifications indicated & visible identification marks on the fire alarm control panel display. we are waiting for RSC T&CVI. | Aug 29 2016 | On 17.10.2017: In progress. Design has been reviewed from Alliance and installation is completed, only T&C is balanced. On 30/04/2019: T&Cx is pending. On 15-03-2021: Corrected. During inspection no such notification was observed. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 14 2016 | Corrected
Initial Inspection |  | 5 | The maximum travel distance to reach an exit of Main Factory Building-1 is approximately 300 ft. | Provide some combination of adding/adjusting exits within 45 m (147.6 ft) to any point on the floor, and/or adjust building protective systems (fire alarm, standpipe, sprinklers) for compliance with Alliance Standard Sections 6.13.1, 6.13.1.1, or 6.13.1.2. | The management setup exit door of production building-1 for maximum travel distance west and east both side. Factory production Building - 1 has eight (8) fire exit doors. | Aug 25 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. Factory management has made three more exits with all compliant features. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 6 | Steel sliding doors, each 8 ft in width, for the means of egress are provided on the South-East and East exterior of Main Factory Building-1. | Replace non-compliant doors and frames in the means of egress with side-swinging doors. Door swing must be in the direction of travel. Replacement doors shall be a minimum width of 0.8 m (32 in), and are listed, approved, self-closing, fire rated door assemblies (door and frame) with latching panic hardware. | The management replace fire door on the South-East and East exterior of Main Factory Building-1. | Aug 21 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 7 | Landings are not provided on both sides of the doors that are used along the path of egress in the Utility Building, or on the ground floor of the Canteen & Storage Building. | Revise the door arrangement so that the doors do not swing out over the stairs for compliance with Alliance Standard Section 6.8.5. | Landings are provided on both sides of the doors that are used along the path of egress in the Utility Building. | Sep 13 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 8 | Only 17 workers have been trained and certified in fire fighting, first aid, and rescue training by the FS&CD authority. | Provide training and certification for the required number of people (25% of total workers) in fire fighting, first aid, and rescue training by an appropriate authority in accordance with the Alliance Safety Training Curriculum. | Factory Management pay to Bangladesh fire service & civil defence for 05 batch training, each batch 40 persons, Already 02 batch training completed. Rest will be continuous Program. On other hand Factory fire fighter trained by Alliance 810 persons. | Dec 1 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 9 | Openings through rated walls were noticed at the entrance to exit stair-1 & -2 in the Office Building. Doors to these stairs were also found provided with glass doors. Penetration of electrical cable through the rated wall of stair enclosure in Main Factory Building-2. | Provide fire-resistive rated opening or penetration protection for rated walls and assemblies in accordance with Alliance Standard Sections 4.6 and 4.7. Consult a qualified fire protection engineer to design the required opening or penetration protection systems. | Openings through rated walls were protected at the entrance to exit stair-1 & -2 in the Office Building. | Sep 15 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 10 | It was noticed that the factory is provided with a Class III Standpipe System but no approved design documents were available at the time of inspection. | Prepare shop drawings and hydraulic calculations (as outlined in NFPA 14) for the installed system and submit to the Alliance for review. Should the existing standpipe system be found to be not in compliance with the design requirements of NFPA 14, modify or replace the system, as needed, for compliance. Prepare revised drawings and calculations for review by the Alliance prior to any modification or installation. | Drawing of standpipe system has Approvable from alliance | Sep 18 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 11 | Notification and initiation devices for the fire alarm system were found to be installed in the facility. It was noticed that smoke detectors were provided in the toilets. No approved design document was provided during the inspection. | Develop and/or provide shop drawings for the installed automatic fire alarm and detection system for the buildings under assessment to the Alliance for review. | We have already correct the CFDS Design Drawing and Include all details as per T&C Report. I will send to RSC on 16th September-21 it for verification & Fedback. | Sep 21 2016 | On 17.10.2017: Design has been reviewed from Alliance and installation is completed, only T&C is balanced. On 30/04/2019: T&Cx is pending. On 15-03-2021: T&C VI found that the system is not approved. For details please see the full T&C VI report. On 16/11/2021: T&CVI found that Final verification is required for FADS On 14/02/2022: Reportedly, modification work is ongoing. On 14/08/2022: Corrected. The T&C Final Verification has been conducted. The System has been approved. For details see the T&C Final Verification report. On 13-05-2024: Corrected. System has been found active where MCP has been tested and found that its actuate the notification appliances properly. Sound level has been found adequate. As built drawing has been found not updated and not matched with the as built system condition (4 storied building toilet area), device quantity requires to update, exhaust fan has been found not interfaced with FACP, Trouble (Loop Driver Open ckt) has been identified on FACP, installation of initiating device and notification appliance has been found not as per manufacturer's published guideline and NFPA-72 . Factory shall ensure that as built drawing matches with the as built system condition, maintenance has been done as per NFPA-72 and the system is free from abnormal condition. Failed to maintain the system as per the requirements of NFPA-72, manufacturer's published guideline and RSC Technical Guidelines Standard may requires partial T&CVI further. | Sep 30 2016 | Corrected
Initial Inspection |  | 12 | An electrically driven fire pump and a diesel operated standby fire pump of 500 gpm at 6.5 bar capacity were found installed for the facility, but no documents were available regarding listings of the pump. The pump is located on the ground floor of the Canteen & Storage Building without any separation from storage areas or the maintenance workshop. The exhaust of the diesel engine is within the pump room. | Prepare shop drawings and hydraulic calculations for the installed system and submit to the Alliance for review. Should the existing fire pump arrangement be found to be not in compliance with the design requirements of NFPA, modify or replace the system, as needed, for compliance. Prepare revised drawings and calculations for review by the Alliance prior to any modification or installation. Also the fire pump shall be provided with fire-resistive rated construction barriers in accordance with the standard. | Factory has made a separated positive section fire pump room. | Sep 17 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 13 | Training programs are not implemented and documented in accordance with the Alliance Safety Training Curriculum. | Implement training programs and document in accordance with the Alliance Safety Training Curriculum. | Already factory management implemented training programs and kept the training documents in accordance with the Alliance Safety Training Curriculum. | Jul 27 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Aug 15 2016 | Corrected
Initial Inspection |  | 14 | No documents were available related to the inspection, testing, or maintenance of the fire extinguishers. | Establish an inspection, testing, and maintenance program for all fire extinguishers and prepare proper documentation. Program must comply with NFPA 10. | Already factory management established an inspection, testing, and maintenance program for all fire extinguishers and kept proper documentation. | Nov 1 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 15 | Occupant loads are not posted at exit access doorways of the buildings under assessment, or at the assembly points. | Post the occupant load for all assembly and production floor areas in a conspicuous space near the main exit or exit access doorway for the space in accordance with Alliance Standard Section 6.4.4. | The occupant load shall be posted for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space. | Jul 2 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Jul 31 2016 | Corrected
Initial Inspection |  | 16 | No documents were provided indicating monthly or annual functional tests of the means of egress illumination were conducted. | Develop a testing and maintenance program that ensures the emergency power for all egress lighting is verified at least once per year. If battery-operated lights are used, these lights shall be tested on a monthly basis. Functional testing of battery powered lights shall be provided for a minimum 30 min once per year. | Factory Management ensure indicating monthly or annual functional tests of the means of egress illumination were conducted. | Jul 26 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Aug 15 2016 | Corrected
Initial Inspection |  | 17 | Handrails for 2 stairs in the Canteen & Storage Building and Stair-1 of Office Building are not provided with handrails on either side. | Provide handrails on both sides of each stairway. Mount new handrail at a height consistent with existing height (between 30 in. and 44 in). The spacing between vertical members will not exceed 200 mm (8 inch). | Handrails are provided on both sides of each stairway. | Nov 12 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Referred to issue no 34. | Dec 31 2016 | Corrected
Initial Inspection |  | 18 | Illuminated exit signs are provided at entrances to exits, but not for changes in direction on the ground floor of Main Factory Building-1 and the ground floor of Main Factory Building-2. | Provide continuously illuminated exit signs per Alliance Standard Section 6.11. Signs shall be placed at all required exits and along egress paths, especially where there is a change in direction for the path of travel. | Illuminated exit signs are provided at entrances to exits, but not for changes in direction on the ground floor of Main Factory Building-1 and the ground floor of Main Factory Building-2. | Nov 23 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 19 | No documents were available related to monthly testing or functional testing of battery powered signs. | Develop a testing and maintenance program that ensures the emergency power for exit signs is verified at least once per year. If battery-operated signs are used, these signs shall be tested on a monthly basis. Functional testing of battery powered signs shall be provided for a minimum 90 min once per year. | Factory management implemented exit sign & fog light checking system periodic basis each month. | Jul 2 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Jul 15 2016 | Corrected
Initial Inspection |  | 20 | The occupiable roof of the Office Building was found to have a parapet wall with a height of 32 in. | Provide parapets or guards with a minimum height of 1067 mm (42 in.) for all occupiable roof areas in accordance with Alliance Standard Section 6.12. | Factory management built a parapets or guards wall height 43 inch. for all occupiable roof areas in accordance with Alliance Standard Section 6.12. | Sep 21 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 21 | Storage of fabric materials under the cutting tables located on the ground floor of Main Factory Building-1 was noticed. | Remove all combustibles stored underneath the cutting tables in accordance with Alliance Standard Section 13.7.2. | Factory management ensure not storage combustibles materials underneath the cutting tables. | Jun 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Jul 15 2016 | Corrected
Initial Inspection |  | 22 | The spot removing room located on the south side of the 1st floor of Main Factory Building-2 is provided with non-rated Thai- Al glass wall and a non-rated ceiling. The fire pump in the Canteen & Storage Building is not separated from storage areas or the maintenance workshop. | Provide fire-resistive rated construction barriers (with associated opening protection) between hazard types in accordance with Alliance Standard Sections 3.4 and 4.5. Consult a qualified fire protection engineer to design the required rated construction barriers. | The spot removing room located on the south side of the 1st floor of Main Factory Building-2 will be shifted. Work in progress. | Nov 1 2016 | Corrective action plan shall have to be completed as per the recommendation. On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 23 | No documents were available related to the inspection, maintenance, or testing procedures of the standpipe and hose system. | Establish an inspection, testing, and maintenance program for the standpipe system. Program must comply with NFPA 25. Any newly installed standpipe system needs to be evaluated for compliance with the design pressure and flow demands of NFPA 14 or BNBC Section 5.4.3. | The standpipe and hose system inspection & testing procedure documents are available at factory. | Nov 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 24 | Only Fire License was available during the inspection. Boiler License, Generator License, or Waiver Certificate, and ABC License for Electrician were not provided. | Apply to appropriate authority in an expeditious manner for issuance of all applicable licenses. | Factory has all applicable permits up date including Fire License & ABC License for Electrician, excluding Boiler & Generator License. Already factory management applied to appropriate authority for issuance Boiler License & Generator License. | Jul 2 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Aug 15 2016 | Corrected
Initial Inspection |  | 25 | No documents were available related to the inspection, maintenance, or testing procedures for the fire pump. | Establish an inspection, testing, and maintenance program for the fire pump. Program must comply with NFPA 25. | Factory has available documents of testing procedures of the fire pump. | Sep 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 26 | Stair designation signs are not provided at each floor entrance from the stairs to the floors of the buildings in English and Bengali. | Install signage adjacent to each stair door indicating the stair name and the floor level in both English and Bengali. | Factory has posted stair designation signs at each floor entrance from the stair to the floor in English and Bengali. Signs indicate the name of the stair and the floor level. Signs has posted adjacent tothe door. | Jul 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Aug 15 2016 | Corrected
Initial Inspection |  | 27 | No occupancy certificates were provided for any building. | Apply to appropriate authority in an expeditious manner for issuance of the Certificates of Occupancy for each building and ancillary structure according to building use. | The factory management already applied to PWD for Occupancy Certificate on 13/02/2017. | Apr 30 2017 | N/A On 17.10.2017: N/A. On 30/04/2019: N/A. On 15-03-2021: N/A. On 14/02/2022: N/A. On 13-05-2024: N/A | Aug 15 2016 | Corrected
Initial Inspection |  | 28 | There was no documentation indicating that Fire Department pre-planning activities have been completed. | Complete Fire Department pre-planning activities with the local Fire Service and Civil Defence in accordance with Alliance Standard Section 13.1.1(2). | Fire Department pre-planning has been completed. | Sep 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Sep 30 2016 | Corrected
Initial Inspection |  | 29 | Hot-work permit program has not been established. | Develop a hot work permit program. The program must comply with the requirements of NFPA 51B. | Already Factory Management has been established hot-work permit program. | Nov 1 2016 | On 17.10.2017: Corrected. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Dec 31 2016 | Corrected
Initial Inspection |  | 30 | Signage for hose stations, hose connections, and for Hydraulic Design Information was not noticed during the survey. | Install signage at required locations and on required equipment. Signage must comply with NFPA 14. | Factory Management signage for the standpipe system installed at required locations and on required components. As per instruction of 1st RVV inspector of Fire. | Dec 1 2016 | On 17.10.2017: Corrected as per site observation. On 30/04/2019: Corrected. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Aug 15 2016 | Corrected
Follow Up Inspection |  | 31 | New finding ( 2nd follow-up): Proper fire evacuation maps is not posted at the entrance of mezzanine floor. | Proper fire evacuation maps shall be posted at the entrance to each exit stair. | already we haveposted evacuation maps at the entrance to each exit stair. we are waiting for RSC T&CVI. Update on 09/07/2025 : Already we have posted update fire evacuation maps at the update for Shed-1 & 2 all entrance to each exit & stair. | May 30 2019 | On 30/04/2019: New finding. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Issue reopened. Evacuation map is required to update for Shed-1 and 2. RPO Comments on 5 May 25: This issue will be verified on the next FUIN. | within 1 month | Pending Verification
Follow Up Inspection |  | 32 | New finding ( 2nd follow-up): The egress path along means of egress has interrupted by storage. | Keep egress paths and stairs clear of storage. | Already we have cleared all egress paths obstacle from the aisles, we have provided effective training to the all workers & staff about evacuation during the emergency and we have ensured floors are smooth as early as possible. Now it is strongly monitoring every day production & compliance team.we are waiting for RSC T&CVI. | May 3 2019 | On 30/04/2019: New finding. On 15-03-2021: Corrected. On 14/02/2022: Corrected. On 13-05-2024: Corrected | Immediately | Corrected
Follow Up Inspection |  | 33 | New finding (3rd illow-up): Areas used for combustible storage are not separated by fire-rated construction at shed-2 (1st floor). | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Where separate storage rooms are not feasible, provide defined storage areas and limit the storage arrangement as follows: - Maximum height of 2.4m and maximum area of 23m2 - If sprinkler protected: maximum height of 3.66m and maximum area of 93m2 Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | We have already removed all storage items that area. we will use the area for another purpose. Update on 09/07/2025 : We have already removed all storage items from (1st floor) shed-2 we will use the area for another purpose. | Jul 30 2024 | On 15-03-2021: New Finding. On 14/02/2022: Corrected. In process storage was found within limit during inspection. On 13-05-2024: Issue reopened. In process storage has been found on 1st floor of Shed-2. RPO Comments on 5 May 25: This issue will be verified on the next FUIN. | Within 3 months | Pending Verification
Follow Up Inspection |  | 34 | New Finding (5th FUI): Handrail/ Guard has not been provided and the guard height is less than 42 inches on Stair-2 of 4 storied building [3rd Floor]. | Provide handrails on both sides of the exit stair and ramp. New and interim handrails shall have a minimum height of 865 mm (34 in.) and a maximum height of 965 mm (38 in.) as measured from the leading edge of the tread. Open guards shall have intermediate rails or pattern such that a sphere 200 mm (8 in.) in diameter cannot pass through any opening up to a height of 865 mm (34 in.) | Update on 09/07/2025 : We have already provided interim handrails on Stair-2 of 4 storied office building 3rd Floor and its height is 42 inches. | Jul 29 2024 | On 13-05-2024: New Finding. RPO Comments on 5 May 25: This issue will be verified on the next FUIN. | within 1 month | Pending Verification
Follow Up Inspection |  | 35 | New Finding (5th FUI): Unauthorized maintenance has been done on Fire Rated door of Shed-1 and 2 so that the integrity of the functionality of fire rated door has not been ensured. | Factory shall ensure that the maintenance work shall be done for the door hardware and accessories on a regular basis as per NFPA 80 and manufacturer's published guideline. Repair/ replace the hardware and accessories which are not functional or under unauthorized maintenance. Doors shall not be tied up with rope or blocked by obstacles. Keep the fire rated doors close all time, if for functional reason require to keep open then interfacing facility with functional FACP shall be ensured | Update on 09/07/2025 : From now onward we will do regular maintenance or Repair our fire doors or replacement of any accessories shall be as per NFPA 80 or manufacturer's published guideline. and our responsible fire team will check daily that all fire doors are active and any fire doors are blocked with rope or bricks. And everyone will be trained in this regard. | Aug 29 2024 | On 13-05-2024: New Finding. RPO Comments on 5 May 25: This issue will be verirfied on the next FUIN. | Within 2 months | Pending Verification
Follow Up Inspection |  | 36 | New Finding (5th FUI): The main structural element of the Shed-2 (Interim Construction) is constructed by steel element which is non-rated and were found in exposed condition without fire protection. | Interim building shall be type-1 or type-2 construction as per Table 3.2.4 of BNBC-2006. Provide required fire rating on the structural elements by following Section 4.4 and Table 4.4.1 of the RSC Technical Guidelines Standard or Table 3.3.1 and Table 4.1.1 from BNBCPart 4. Prior to install any Passive Fire Protection System, share the design philosophy, product datasheet and certificate , proposed drawing and other supporting documents to RSC for review. | Update on 09/07/2025 : We are appoint consultancy team; they have already prepared a drawing for fire protection system and we will send this drawing to the RSC team in a separate email for review and approval, we will start the next work after the fire drawing is approved by the RSC. | Dec 27 2024 | On 13-05-2024: New Finding. RPO Comments on 16 Jul 25: This RSC is waiting for the required doc and remediation completion information from the factory. No drawing received yet. | Within 6 months | In Progress

## Electrical
Date
03-Nov-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED, South Gouripur, Savar
Date of Inspection |  | 2016-05-16
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Switchboards and/or distribution boards do not have minimum clearance of 1 m (39 in). | Provide minimum clearance of 1 m (39 in) in front of all panel boards in accordance with the Alliance requirement. | Management ensure minimum clearance in front of all panel boards in accordance with the requirement. | Aug 25 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 2 | Readily accessible single point of disconnect is not provided for each main electrical service feed. | Provide readily accessible single point of disconnect for each main electrical service feed. | Factory Electrical Engineer check and ensure readily accessible single point of disconnect for each main electrical service feed. | Aug 20 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 3 | All metal in the building is not connected to the building earthing/grounding system. | Survey the entire building to identify all locations of non compliance. Connect all metal in the building to the building earthing/grounding system, such as metal rebar in concrete, metal frame of building, or metal water pipe. | Management connected all metal in the premises to the building earthing/grounding system. | Aug 16 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 4 | Shielding or additional insulation is not provided for wiring exposed to external heat sources. Location: Boiler room. | In order to avoid the effects of heat from external sources one of the following methods should be used to protect wiring systems: (1) shielding; (2) placing 900 mm (36 in.) from the source of heat; (3) local reinforcement or substitution of insulating material. | To avoid the effects of heat use additional Insulation metal pipe. | Aug 17 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 5 | The generator exhaust discharges to the exterior of the building, but it is not in a safe location. | Provide the generator exhaust discharge to the exterior of the building in accordance with Alliance standards. | Management completed work for Generator exhaust discharge to the exterior of the building. | Aug 20 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 6 | Underground service cables are not laid in conformity with the requirements for concealed wiring. | Install underground service lines in accordance with the requirements for concealed wiring. | Underground service cables in accordance with the concealed wiring. | Sep 20 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 7 | Light fixtures without protective covers are installed in storage areas. | Provide light fixtures with protective covers in storage and other areas where the Inspector of the Factories Rules (1.5.3.5) Part 53 prohibits these fixtures. | The building owner claim to us for his personal purposes use this build, on based that we are amendment our deed & changed layout plan, fire lienees. Also we updated Alliance accordingly. | Aug 10 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 8 | Cable trenches are not properly covered. | Provide cable ladder/cable trench to accommodate cable. If trench is provided, then provide the cable ladder/cable trench with a cover of non flammable material. |  | Sep 10 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 9 | Emergency power switchboards, distribution boards, and circuits are not properly identified. | Provide proper identification of all boxes and enclosures (including transfer switches, generators, and power panels) for emergency circuits. Provide permanently markings so they will be readily identified as a component of an emergency circuit or system. The required marking can be by color code, the words “emergency system,” or any other method that identifies the box or enclosure as a component of the emergency system. | Emergency power switchboards, distribution boards, and circuits are properly identified. | Sep 10 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 10 | The factory does not have any lightning protection system installed. As per risk index calculation, the factory needs to install lightning protection system. | Have a qualified electrical engineer design a lightning protection system in accordance with NFPA-780. Have a licensed electrician install the designed system. | LPS was approved by Alliance and installed as per approval. | Feb 1 2017 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 11 | Service cable erection is not proper. Location: Near substation room. | Provide protection from water damage in accordance with the Alliance Standard. | Service cable properly erecting . Location: Near substation room. | Jul 13 2016 | On 17/10/2017: Corrected. No such problem found during inspection. | Aug 31 2016 | Corrected
Initial Inspection |  | 12 | Wooden boxes are stored within the substation room near HT panel. | Remove all combustible materials within the substation room. | Management strictly noticed don't use Combustible material in substation room. Also management follow-up this work regularly. | Jul 13 2016 | On 17/10/2017: Corrected. | Jul 30 2016 | Corrected
Initial Inspection |  | 13 | Circuits are drawn for loads without the incorporation of a overcurrent protection device (circuit breaker). Multiple cables are connected in all Dbs. Location: shed building. | Provide circuit breaker (protective device) to control each circuit individually. | Circuits are drawn for loads without the incorporation of a overcurrent protection device (circuit breaker). | Sep 27 2016 | On 17/10/2017: Corrected. No such problem found during inspection. | Aug 31 2016 | Corrected
Initial Inspection |  | 14 | Higher rated breaker with lower rated wiring was found in a distribution board. Location: Shed building ground floor. | Consult with a qualified Electrical Engineer and ensure electrical wiring/cables are sized according to capacity of circuit breakers. | We have replaced all higher rated breaker by actual rated breaker as per advice our consultant with a qualified Electrical Engineer. | Aug 20 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Not Corrected. Work is going on. They have changed some circuit breakers and still not competed. On 30/04/2019: Not Corrected. On 29/09/2020 (RSC): Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 15 | Multi looping of wiring/cables was observed at circuit breakers within switchboards and distribution boards. Location: shed building. | Remove multi looping of wiring/cables at circuit breakers within switchboards and/or distribution boards. Make separate connection from bus bar for individual circuits. | No Multi looping of wiring/cables were observed at circuit breakers and bas bar within switchboards and/or distribution boards. | Jul 26 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 16 | Switchboards and distribution boards are not installed in compliant locations. Location: office building under stair, Shed building stair. | Relocate distribution boards to suitable locations for operation and maintenance. |  | Oct 16 2016 | On 17/10/2017: Corrected. No such problem found during inspection. | Aug 31 2016 | Corrected
Initial Inspection |  | 17 | Proper as built diagram was not present on site. | Have a qualified electrical engineer develop as-built drawings detailing key components and capacity of the electrical system in accordance with Alliance requirements. | As-built electrical drawings indicating information such as panel and circuit locations throughout the building(s) available for review. | Sep 6 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. During inspection the SLD was found as-built. | Aug 31 2016 | Corrected
Initial Inspection |  | 18 | The workers that operate and maintain the electrical system did not receive any electrical safety training. | Develop and implement an electrical safety program. Include key topes such as lock-out tag-out procedures, personal protective equipment requirements, etc. Reference NFPA 70E for example program requirements. | Workers have operate and maintain the electrical system received electrical safety training & training documentation available for review. | Sep 4 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Not Corrected. The training documents are updated. However, no policies for using LOTO or insulated tools are found. On 30/04/2019: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 19 | All equipment is not efficiently earthed and properly connected to the required number of earth electrodes. | Provide efficient earthing for all equipment at required locations and properly connect using the required number of earth electrodes. Refer to the BNBC for required number of electrodes. | All equipment are efficiently earthed and properly connected to the required number of earth electrodes. | Jul 6 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 20 | Thermographic scans of electrical equipment have not been completed every three years. | Complete Thermographic scans on a minimum three year cycle. Thermographic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment and NFPA 70B or a comparable standard. | Thermographic scans of electrical equipment have been completed on dated : 11/08/2016. | Aug 11 2016 | On 17/10/2017: Not Corrected. Hot spot found on site. On 26/06/2018: Not Corrected. Found a report but not properly informative. The report does not have all information (the temperature range of the image). On 30/04/2019: Not Corrected. On 29/09/2020 (RSC): Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 21 | Switchboards and distribution boards are not provided with the physical means to prevent the installation of more over current devices for which the panel board was designed, rated, and listed. Location: All boards. | For switchboards and/or distribution boards, provide the physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed following NFPA 70 section 408.54. Verify the existing load does not exceed the panel rating. | Switchboards /distribution boards are provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Aug 31 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 22 | Multiple cables are connected in all Dbs. Location: shed building. Also, all internal components of switchboards and distribution boards are not properly concealed. | Provide covers or blanks to conceal all live internal components of switchboards and/or distribution boards. | All internal components of switchboards/distribution boards are properly concealed (No missing circuit breaker or knockout covers). | Aug 10 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 23 | All switchboards and distribution boards are not properly grounded to the earth bar. | Provide proper grounding for switchboards and distribution boards utilizing proper size of earthing cables and sufficient number of earth electrodes. | All switchboards and distribution boards are properly grounded to the earth bar. | Aug 10 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 24 | Switchboards or distribution boards do not have clear identification marking. Location: All boards. | Provide clear and permanent identification marks on all distribution boards, switchboards, sub main boards and switches and post proper caution/danger signage in all electrical panel boards. | Switchboards / distribution boards have clear identification markings. | Aug 10 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Not Corrected. This shall be permanent legible marking according to SLD. Only few panels do not have this permanent marking. On 30/04/2019: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 25 | Electrical wiring/cables are not properly identified. | Provide identification of wires/cables by separate color coding, marking tape, tagging, or other approved means. | Electrical wiring/cable is properly identified. | Sep 29 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 26 | Junction boxes and other electrical devices are not provided with covers. | Provide adequate covers for all junction boxes and other electrical devices. | Junction boxes and other electrical devices are provided with covers. | Jul 13 2016 | On 17/10/2017: Corrected. No such junction box found during inspection. | Aug 31 2016 | Corrected
Initial Inspection |  | 27 | Cable sockets are not provided for stranded conductors. | Provide proper size and type of cable socket for stranded conductors having a nominal cross-sectional area 6mm2 or greater. For conductors below 6 mm2 without cable sockets, provide soldering for all strands at the exposed ends or crimp the exposed ends using suitable sleeve or ferrules. | Cable sockets are provided for stranded conductors. | Aug 22 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 28 | Cable joints are not through porcelain/PVC connectors. | Provide cable joints through porcelain/PVC connectors with PIB tape wound around joint before placing the cable in the box. | All cable joints rechecked and ensured joints properly. | Sep 26 2016 | On 17/10/2017: Corrected. No splicing joint found. | Aug 31 2016 | Corrected
Initial Inspection |  | 29 | The substation room does not have adequate means of security. | Install security measures to ensure access to the substation is restricted. | The substation room has adequate means of security | Jul 4 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 30 | Transformer are grounded with the same bar of system earthed bar. | Provide two earthing (body earthing) connections to two different and distinct points on the transformer. | Transformers has properly grounded (earthed). | Oct 3 2016 | On 17/10/2017: Corrected. Earthing bar separated. | Aug 31 2016 | Corrected
Initial Inspection |  | 31 | All electrical wiring/cable is not properly terminated at its point of termination. Unterminated wires were found inside the board. Location: Shed building - ground floor. | Provide proper termination of all wiring in accordance with the Alliance standard. No Unterminated wires or cables are allowed. | All electrical wiring/cable are properly terminated at its point of termination. | Aug 18 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 32 | Switchboard and distribution boards have no capacity information label. Location: All boards. | Provide capacity information labels (Maximum current rating, number of circuit breakers, rated capacity of circuit breaker, etc.) for Switchboards and/or distribution boards. Display panel schedule on panel door (inner side) printed on a sheet made of non-combustible material. | Capacity information label attached on all Switchboard and distribution boards. | Aug 29 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 33 | Test report was not provided during audit, so it cannot be determined without the test report of the transformers. | Conduct a complete oil analysis to determine the content of PCBs in transformer oil and consider replacing transformers found with harmful substances to reduce health hazards. | The management has tested Transformer & oil. We attached Transformer Certificate & Transformer Oil test report. | Nov 15 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. It is advised to conduct the test from any govt authority (power distribution). | Aug 31 2016 | Corrected
Initial Inspection |  | 34 | No Periodic safety inspections of the electrical system components were completed or documented. | Establish a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Maintain records concerning inspections and follow up actions. | Management Established a periodic inspection program to ensure the electrical systems are free from damage, debris, dirt, lint, etc. Sr. Manager Utility monitoring this program & follow up actions & electrician maintain records concerning inspections. | Aug 29 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 35 | Electrical wiring and conduit is not properly supported to prevent excessive bending or physical damage. Location: Transformer room. | Survey all wiring and conduit to identify all locations where it is not properly supported and protected from physical damage. Provide adequate supports for electrical wiring and conduit. Consult a qualified electrical engineer for required remediation work and selection of appropriate materials. | Already The company has an appointed B.S.C engineer of Electrical. He was completed remediation work by appropriate materials. Now Electrical wiring and conduit is properly supported to prevent excessive bending or physical damage. | Aug 18 2016 | On 17/10/2017: Corrected. Cables are supported. | Aug 31 2016 | Corrected
Initial Inspection |  | 36 | The generator frame earthing (grounding) is not provided at two separate points. | Provide generator frame earthing at two separate points with proper size of conductors and sufficient number of earth electrodes. | The generator frame provide Earthing at two separate points with proper size of conductors and sufficient number of earth electrodes. | Aug 14 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 37 | Each circuit is not provided with a dedicated neutral. | Provide a dedicated neutral for each circuit following respective phase cable size. Provide identification and marking of neutral cables to each circuit for maintenance. | Provide a dedicated neutral for each circuit following respective phase cable size. | Aug 13 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 38 | The generator room is not appropriately sized in order to properly access the generator to perform routine maintenance activities. | Ensure all sides have 1 m clearance to properly access diesel generator to perform operation and routine maintenance activities. | Already generator room completed and generator shifted front old place to new constructed room | Apr 30 2017 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 39 | Periodical Insulation Resistance Measurement Program was not found to be established or recorded. | Develop an Insulation Resistance Measurement Program that ensures deterioration of insulation resistance will be identified quickly. Testing should be in compliance with International Electrical Testing Association (NETA). All transformers, switchgears, etc. shall be subject to an insulation resistance measurement test to ground after installation but before any wiring is connected. Insulation tests shall be made between open contacts of circuit breakers, switches, etc. and between each phase and earth. | Periodical Insulation Resistance measurement have completed dated 31 august-2016 | Aug 12 2016 | On 17/10/2017: Corrected. | Jul 31 2016 | Corrected
Initial Inspection |  | 40 | Mechanical guards are not provided for electrical equipment. Location: pump room. | Survey all locations to identify missing mechanical guards. Provide mechanical guards for equipment where necessary. | Mechanical guards are provided for electrical equipment | Sep 22 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 41 | Electrical insulation mats are provided only in LT panel room, not provided on floor for Dbs. | Provide electrical graded rubber insulation mats, specified for 650 V-protection, of required size (accommodating at least two person or dependent on the panel's width) in accordance with Alliance Standards. | Electrical insulation mats are provided in HT panel,LT panel room, and all floor Dbs. | Aug 12 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Jul 31 2016 | Corrected
Initial Inspection |  | 42 | Meters and other electrical devices are only provided in LT panel, but these are not in operation. | Ensure meters and other electrical devices are installed on the main electrical equipment and are operational. | Meters and other electrical devices have installed on the main electrical equipment and are operational. | Aug 31 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 43 | Required equipment and safety signage is not posted within the room. | Provide required safety signage in switchgear, unit substations, transformers, pull boxes, connection boxes, and other similar associated equipment. Signage shall be marked with appropriate caution signs. Entrance to room and other guarded locations that contain exposed live parts shall be marked with conspicuous warning signs forbidding unqualified persons to enter. | Safety signage in switchgear, unit substations, transformers, pull boxes, connection boxes, and other similar associated equipment. Signage shall be marked with appropriate caution signs. | Aug 8 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 44 | Inspection, maintenance, and testing procedures of the UPS are not completed or documented. | Establish an inspection testing, and maintenance program for the Instant Power Supply (IPS) and associated components. The program must based on the following: (1) Manufacturer's recommendations (2) Manufacturer's instruction manuals (3) Minimum Requirements of NFPA 111 Chapter 8 (4) Minimum Requirements of NFPA 70B Chapter 28. | Maintaining inspection testing and maintenance program for the Instant Power Supply (IPS) as per Manufacturer's recommendations, instruction manual and NFPA 70B Chapter 28 also. | Sep 1 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 45 | No fire fighting equipment is installed inside the generator room. | Engage a qualified engineer to confirm the appropriate type and number of fire fighting equipment inside the generator room and install it in accordance with Alliance Standards. | Already installed appropriate type and number of fire fighting equipment inside the generator room accordance with Alliance Standards | Jun 23 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 46 | Inspection, maintenance, and testing procedures for the emergency generator are not completed or documented. | Establish a routine maintenance and testing program for the emergency generator. The program shall be based on all of the following: (1) Manufacturer's recommendations (2) Manufacturer's Instruction manuals (3) Requirements of NFPA 110 Chapter 8 | Maintaining a routine maintenance and testing program for the emergency generator as per Manufacturer's recommendations , instruction manual and NFPA 110 Chapter 8 also. | Aug 25 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 47 | Transformer oil analysis has not been completed on main service transformers. | Perform a transformer oil analysis on applicable transformers at appropriate intervals based on voltage and power. | Transformer oil analysis has been completed on main service transformers dated 15 11 2016. | Nov 15 2016 | On 17/10/2017: Corrected. | Aug 30 2016 | Corrected
Initial Inspection |  | 48 | Signage indicating the prohibition of light fixtures without protective covers is not provided. | Provide signage indicating the prohibition of light fixtures without protective covers (otherwise known as naked lights) at required locations. Signs shall be posted in Bengali and English, at all entrances to these areas. | Signage has been indicating the prohibition of light fixtures without protective covers (otherwise known as naked lights) posted in Bengali and English, | Aug 21 2016 | On 17/10/2017: Corrected. | Aug 31 2016 | Corrected
Initial Inspection |  | 49 | Phase separators are not provided between terminals on circuit breakers. Location: shed building. | Install phase separators between terminal connections. Verify phase separators are installed at all remaining locations. | Already phase separators Installed between terminal connections are installed at all locations. | Jul 31 2016 | On 17/10/2017: Not Corrected. On 26/06/2018: Corrected. | Aug 31 2016 | Corrected
Follow Up Inspection |  | 50 | New Finding; Uninsulated electrical tools are used by maintenance personnel in the factory | For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. |  | Nov 17 2017 | On 26/06/2018: Not Corrected. On 30/04/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Panel base plates are removed to allow cable entry. | Panel base plates must be installed, at all time, and cables entering panel must be firmly fixed with cable gland | We have installed base plates at all the panel board. | Nov 17 2017 | On 26/06/2018: Not Corrected. On 30/04/2019: Not Corrected. On 29/09/2020 (RSC): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Inadequate working space around transformer for performing maintenance work | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained | Space has been increased for maintenance work in the transformer room, and approval has been taken from RSC on 27th February-21 Now the maintenance movement has been made free and the cable trance has been removed. | Aug 30 2018 | On 30/04/2019: Not Corrected. On 29/09/2020 (RSC): Not Corrected. On 15/03/2021: work's been started, but not finished yet. Not Corrected. Maintenance movement is obstacle due to improper cable trench cover On 31-Jan-2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 53 | New Finding: Cable insulation resistance report is generated without conducting any physical survey. Latest report is almost a copy of previous report. | Cable insulation resistance test must be done and recorded at least once in two year. Need to generate the report with real-time images with recommendations (if any). | We are regularly testing cable insulation resistance and keeping record accordingly | Jul 30 2018 | On 30/04/2019: Not Corrected. On 30/04/2019: Not Corrected. Inadequate pictorial evidences to support the report's authenticity. On 29/09/2020 (RSC): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: LPS is not modified according to modified construction. Air terminals are placed at more than 2 ft from corner/edges. All solar panels / water tanks are not protected and all metal connections are not bonded. | LPS installation needs to be modified as the structures are modified at the roof. All air terminals need to be installed at a distance of maximum 2ft from the corner or edges. All water tanks, solar panels and other exposed parts on the roof need to be protected. | We have modified the LPS installation as per alliance approved Design. | Jul 30 2018 | On 30/04/2019: Not Corrected. On 29/09/2020 (RSC): Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding (RSC): Electrical SLD is not properly informative. Load detail, load schedule and earthing layout is required. | Draw as built electrical SLD mentioning all required information . Electrical SLD must be updated properly when electrical system is modified. |  | Nov 10 2020 | On 15/03/2021: work's been started, but not finished yet. Not Corrected. SLD submitted to RSC On 31-Jan-2022: Not Corrected. Work is going on. On 14/06/2023: Not Corrected. Factory is working on earthing system as per accepted ELD. Again, Breakers information, Circuits and equipment identification have been done as per accepted SLD. On 11/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: PPE, insulated electrical tools & LOTO (Lock-Out-Tag-Out) devices are inadequate for maintenance work. Electric safety training program document is not enriched enough | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs.(Factory may follow NFPA 70E) | already we started a training program on the PPE and introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure the safety of the personnel during any maintenance and keep all records of using LOTO. We provided an Electrical insulation Rubber mat which is not less than 3 mm thick at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated types of machinery). we ensured each electrical distribution board/panel are easily accessible. | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding Air terminal are missing at several points of Lightning Protection System. | Missing Air Terminals shall be reinstalled. | we have reinstalled the missing air terminal accordingly. | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present Inadequate rubber (insulation) mat at the working area of distribution board/panel. Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work. | CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location Electrical insulation (not less than 3 mm thick in case of rubber mat) at the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries) must be ensured. Each electrical distribution board/panel must be easily accessible. In case of height its top shall not be higher than 2m from base; and door opening shall be at least 90 degree. | CPR instruction is already hung near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible locations. | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Cable termination at the motor terminal box is directly connected to terminals without proper gland. Wooden support used for electrical installation/element. | All equipment termination must be done with proper termination including cable glands to avoid ingression of moisture and dust entering the terminals. Remove combustible materials(wooden plunk) | we have installed the cable gland properly and removed all combustible materials. | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 60 | New Finding Wiring using flexible/rigid PVC pipe- this arrangement does not have any support for cables Power Cables are hanging without proper support. | A cable ladder must be used; if it is routed through outside wall, either the cable ladder must be covered or a cable duct must be used | We used a cable ladder routed over the inside of the tray, and it has been covered. | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding Cable duct/channels are filled with fluffs (Lint/dust). Combustible materials are tied with BBT | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. Combustible materials shall be removed from electrical system. | We have completed the cleaning works of the cable channels. | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding Both transformer Neutral earthing (system earthing) & body earthing (equipment earthing) connection is inadequate. | Equipment earthing cable size shall be increased. The earth cable size shall be less than or equal to half of the phase cable/adiabatic calculation (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. |  | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Not Corrected. Factory is working on earthing system as per accepted ELD. On 11/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding Lead acid battery terminals are left open Generator output box has openings. | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. Unwanted openings shall be sealed | we have installed Lead-acid battery terminals that must be covered/capped and rust must be checked and cleaned and Unwanted openings. | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding Equipment earth cable (for generator) size is inadequate. | Equipment earth connection for generator shall be drawn from at least two separate point of generator; and the cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. |  | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Not Corrected. Factory is working on earthing system as per accepted ELD. On 11/03/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: Compressed airline run through the enclosed cable raceway. | Raceways or cable trays containing electrical conductors shall not have a foreign system (e.g. steam, water, air, gas, drainage) other than electrical. Segregate the airline and power line and use different support for each. | We have completed segregating the airline and power line by using different support. | Apr 25 2021 | On 31-Jan-2022: Not Corrected. On 14/06/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding MDB room has inadequate ventilation & inadequate illumination | Adequate ventilation must be maintained in MDB room. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. Ensure adequate illumination in the MDB room thus any maintenance can be done comfortably (150 lux shall be maintained). | we have completed the adequate ventilation in the MDB room. ensured the Cross/forced ventilation by For exhaust fan, which is must not less than 8". | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding Phase barrier/separators are inadequate | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it) | We have completed the phase separated by insulator as per requirement. | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding Insulation resistance test of electrical power cables is manipulated(Data randomly copied & report has inadequate pictorial evidence) | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | We have completed the Insulation resistance test as per requirement and recorded. | Apr 25 2021 | On 31-Jan-2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Wiring inside the storeroom is not secured. | Secure cabling shall be ensured in storeroom (use electrical connection through secure path e.g. GI steel pipe/metal flexible pipe and switches should be placed outside of the room). | We have completed securing the store line by using metal flexible and removing all insecure lines. | Mar 9 2022 | On 14/06/2023: Corrected. | 1 Month | Corrected