## Structural
Date
10-Nov-2025 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED (EXTENSION), South Gouripur, Dhaka, Dhaka
Date of Inspection |  | 2025-02-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Lack of design report (RACK Shed). | The building engineer is required to prepare design report in compliance with section 1.9.1 (part-6, BNBC). | Update on 20/05/2025 : We are appoint consultancy team; they are working to prepare design document, design report, and a set of structural drawings, as per RSC guideline. We will complete work in RSC timeline and send to RSC team in email for review and approval. | Jul 1 2025 | On 16-Oct-2025: The factory has not started work yet. The factory is required to prepare the design report and submit the report to the RSC without futher delay. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 2 | Lack of design report (RACK Shed). | Implement remediation work if required. | Update on 20/05/2025 : We are appoint consultancy team; they are working to prepare design document, design report, and a set of structural drawings, as per RSC guideline.After receive reports if suggest any remadition work we will complete it. | Nov 20 2025 | On 16-Oct-2025: After acceptance of the design report, the factory is required to complete the required remedial works. Progress Status: 0% | Within 6 Months | In Progress
Initial Inspection |  | 3 | Distorted bracing on steel racks (RACK Shed). | The building engineer is required to replace distorted bracing of steel racks. | Update on 20/05/2025 : We already contact with a Rack materials suppliers. After receive rack materials we will replace distorted bracing of steel racks in RSC timeline. | Jul 1 2025 | On 16-Oct-2025: No action has been taken yet; the factory is required to replace the distorted bracings as per the specification. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 4 | Missing bolt in steel connections (RACK Shed). | The building engineer is required to install the missing bolt. | Update on 20/05/2025 : We will install all missing bolt within RSC timeline. | Jul 1 2025 | On 16-Oct-2025: No action has been taken yet; the factory is required to investigate and identify the locations and reinstall the missing bolts as per the specification. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 5 | High stress in flat slab that requires immediate design review (Female Toilet Building) | Take minimum 4 concrete cores (100 mm diameter) from both column and flat slab to verify in-situ concrete strength. | Update on 20/05/2025 : We have contacted with a consultant ,who also work for collecting and testing concrete cores to assess the quality and strength of existing concrete structures.After complete concrete core test work and receive report from consultant we will send it to RSC for review . | Jun 4 2025 | On 16-Oct-2025: The factory took two concrete cores from the column and two from the flat plate. During the inspection core test report was found on site. The factory is required to take two additional cores from the column and two cores from the slab. Progress Status: 50% | Immediate | In Progress
Initial Inspection |  | 6 | High stress in flat slab that requires immediate design review (Female Toilet Building) | The building engineer is required to check the adequacy of flat slab and prepare a Detailed Engineering Assessment (DEA). Submit DEA documents to the RSC for review. | Update on 20/05/2025 : We are appoint consultancy team; they are working to prepare Detailed Engineering Assessment (DEA).After Complete DEA report we will send it to the RSC team for review and approval. | Jun 4 2025 | .On 16-Oct-2025: The factory has not started work yet. The factory is required to prepare the DEA report and submit the report to the RSC without futher delay. Progress Status: 0% | Immediate | In Progress
Initial Inspection |  | 7 | High stress in flat slab that requires immediate design review (Female Toilet Building) | Produce and actively manage a floor load plan. | Update on 20/05/2025 : We are appointed consultancy team; they are working to prepare design report and give us floor load plan. We will complete within RSC timeline and send to RSC team by email for review and approval. | Jul 1 2025 | On 16-Oct-2025: Load plan not prepared yet. The factory is required to prepare the load plan, DEA report and submit the report to the RSC without futher delay. During the inspection, the loading was found below 2 kPa. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 8 | High stress in flat slab that requires immediate design review (Female Toilet Building) | Implement remediation work if required. | Update on 20/05/2025 : We are appointed consultancy team; they are working to prepare design report and give us floor load plan. After receive reports if suggest any remadition work we will complete it. | Jul 1 2025 | .On 16-Oct-2025: After acceptance of the design report, the factory is required to complete the required remedial works. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 9 | High stress in flat slab that requires immediate design review (Female Toilet Building) | Implement floor load plan. | Update on 20/05/2025 : We are appointed consultancy team; they are working to prepare design report and give us floor load plan. We will complete work in RSC timeline and Implement floor load plan. | Jul 1 2025 | .On 16-Oct-2025: Load plan not prepared yet. The factory is required to prepare the load plan, DEA report and submit the report to the RSC without futher delay. During the inspection, the loading was found to be 2 kPa. Progress Status: 0% | Within 6 Weeks | In Progress
Initial Inspection |  | 10 | Dampness on a brick wall (Female Toilet Building). | The building engineer is required to repair the dampness with a suitable method. | Update on 20/05/2025 : We are searching for dampness repair paint and related materials to repair dampness of wall. we will repair the dampness with a suitable method in RSC timeline. | Jul 1 2025 | On 16-Oct-2025: Dampness was found throughout the building. The factory is required to repair the damp areas with a suitable method. Progress Status: 0% | within 6 weeks | In Progress
Initial Inspection |  | 11 | Nonstructural elements found not anchored/braced (Electrical Maintenance Room). | The building engineer is required to anchor/brace all nonstructural elements within the factory. | Update on 20/05/2025 : We are searching for sustainable encore materials to anchor/brace all non structural elements .We will complete work in RSC timeline. | Nov 20 2025 | .On 16-Oct-2025: The factory provided anchorage to the non-structural racks. | within 6 months | Corrected
Initial Inspection |  | 12 | Lack of lateral stability (Multipurpose Shed). | The building engineer is required to check the lateral stability of the shed and prepare an Engineering Assessment (EA) report as per 1.9.1 BNBC. | Update on 20/05/2025 : We are appointed consultancy team; they will check the lateral stability of the shed and prepare an Engineering Assessment (EA) report of our Multipurpose Shed as per 1.9.1 BNBC .We will complete work in RSC timeline and send to RSC team in email for review and approval. | Jul 1 2025 | .On 16-Oct-2025: The factory has not started work yet. The factory is required to prepare the EA report and submit the report to the RSC without futher delay. Progress Status: 0% | within 6 weeks | In Progress
Initial Inspection |  | 13 | Lack of lateral stability (Multipurpose Shed). | Implement remediation work if required. | Update on 20/05/2025 : We are appointed consultancy team; they will check the lateral stability of the shed and prepare an Engineering Assessment (EA) report of our Multipurpose Shed as per 1.9.1 BNBC . After receive report from consultant we will review it and if suggest any remadition work we will complete it. | Nov 20 2025 | .On 16-Oct-2025: After acceptance of the design report, the factory is required to complete the required remedial works. Progress Status: 0% | within 6 months | In Progress
Initial Inspection |  | 14 | Lack of lateral stability (Workers Dining Hall). | The building engineer is required to check the lateral stability of the shed and prepare an Engineering Assessment (EA) report as per 1.9.1 BNBC. | Update on 20/05/2025 : We are appointed consultancy team; they will check the lateral stability of the shed and prepare an Engineering Assessment (EA) report of our Workers Dining Hall shed as per 1.9.1 BNBC .We will complete work in RSC timeline and send to RSC team in email for review and approval. | Jul 1 2025 | .On 16-Oct-2025: The factory has not started work yet. The factory is required to prepare the EA report and submit the report to the RSC without futher delay. Progress Status: 0% | within 6 weeks | In Progress
Initial Inspection |  | 15 | Lack of lateral stability (Workers Dining Hall). | Implement remediation work if required. | Update on 20/05/2025 : We are appointed consultancy team; they will check the lateral stability of the shed and prepare an Engineering Assessment (EA) report of our Workers Dining Hall shed as per 1.9.1 BNBC .After receive report from consultant we will review and if suggest any remadition work we will complete it. | Nov 20 2025 | .On 16-Oct-2025: After acceptance of the design report, the factory is required to complete the required remedial works. Progress Status: 0% | within 6 months | In Progress
Initial Inspection |  | 16 | Absence of bracing system and poor connection (Jhut Boiler). | The building engineer is required to prepare safety check report with a remediation plan incorporating bracing and proper connection. | Update on 20/05/2025 : We are appointed consultancy team; they will check the transfer media, horizontal bracing and vertical bracing and make a report with remediation plan incorporating bracing and proper connection.We will complete work in RSC timeline and send to RSC team in email for review and approval. | Jul 1 2025 | .On 16-Oct-2025: The factory has not started work yet. The factory is required to prepare the safety check report and submit the report to the RSC without futher delay. Progress Status: 0% | within 6 weeks | In Progress
Initial Inspection |  | 17 | Absence of bracing system and poor connection (Jhut Boiler). | Implement remediation work where required. | Update on 20/05/2025 : We are appointed consultancy team; they will check the transfer media, horizontal bracing and vertical bracing and make a report with remediation plan incorporating bracing and proper connection.After receive safety check report we will review it and if suggest some remadition work we will complete it. | Nov 20 2025 | .On 16-Oct-2025: After acceptance of the design report, the factory is required to complete the required remedial works. Progress Status: 0% | within 6 months | In Progress
Follow Up Inspection |  | 18 | New Findings 01: Integration of racks for potential seismic hazard. (Rack Shed) | Building engineer is required to check the requirements of the integration (tie up all racks) of the racks for the potential seismic hazards. The calculation and drawing need to incorporated in the EA report of the RACK SHED. | In Progress | Dec 11 2025 | .On 16-Oct-2025: During the inspection, a multi-level steel rack was found untied. The Building Engineer is required to check the integration requirements (tying up all racks) to address potential seismic hazards. The related calculations and drawings shall be incorporated into the Engineering Assessment (EA) report of the Rack Shed. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 19 | New Findings 02: New structures in factory premises – single storied Wastage Shed (area approximately 300 sft., construction year 2025) Observation: Nonengineered shed (Wastage Shed) | Building engineer is required to provide necessary alternatives to make the structure stable. Otherwise, replace it with an engineered one. | In Progress | Dec 11 2025 | .On 16-Oct-2025: During the inspection, a non-engineered structure was found in factory premises – Single storied Wastage shed. Building engineer is required to provide necessary alternatives to make the structure stable. Otherwise, replace it with an engineered one. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 20 | New Finding-03: New structures in factory premises – [single storied steel Diesel Shed (area approximately 100 sft., construction year 2024)] Observation: Lack of as-built drawings | Building engineer is required to prepare the as built drawings with conncetion details for Diesel Shed and kept at factory site for verification during the next inspection. | In Progress | Dec 11 2025 | .On 16-Oct-2025: During the inspection, one new structure was found in factory premises-Single storied Diesel Shed. As-built drawings were not available. Building engineer is required to prepare the as built drawings with conncetion details for Diesel Shed and kept at factory site for verification during the next inspection. | (within 6 weeks) | In Progress

## Fire
Date
10-Nov-2025 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED (EXTENSION), South Gouripur, Dhaka, Dhaka
Date of Inspection |  | 2025-02-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Rooms used for combustible storage are not separated by fire rated construction. Locations: Ground floor (Jhut Boiler Shed), Idle machine room (Multipurpose Shed). | Rooms used for storage of combustible materials shall be separated from the surrounding occupancy with a minimum 1 hour construction in accordance with section 3.4.2.1.5 of RSC Technical Guideline (Standard). | Update on 20/05/2025 :The management has decided to separate the rooms used for storage of flammable materials from the surrounding areas as per Section 3.4.2.1.5 of RSC Technical Guidelines (Standards). The construction shall be fire rated for at least 1 hour. We will complete the work in RSC time line. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 2 | The main structural elements of the building (peak height 51 ft (15.545m)) are constructed by steel which is non-rated and were found in exposed condition without any fire protection. (Interim Structure). Location: Warehouse Rack Shed. | The construction type is unprotected steel construction. As per RSC Technical Guideline and BNBC 2006, The Fire rating of the structure requires to be confirmed as per BNBC 2006. The "Ministry of Housing and Public Works” has issued a resolution based on the recommendations from the House Building Research Institute (HBRI) and the Public Works Department (PWD) to assess structural fire protection requirements of steel buildings (unprotected non- combustible construction type) according to BNBC 2020. The construction type shall confirm to be in accordance with BNBC 2020 Part-3, Table 3.1.7. Ensure fire resistive rated construction following Table 3.3.1 (a) Part 3 Section-3, Table 3.2.2 and Table 3.2.3 Part 3 Section 2 and Table 4.1.1 from BNBC 2020 Part 4 Section 1. Provide design philosophy to determine the construction type as per BNBC 2020. If any construction rating requires, Consult a qualified fire protection engineer to achieve the require fire rating. Submit the design philosophy along with the required documents to RSC for review the required construction type. Once the design philosophy is reviewed, provide fire ratings of structural members. | Update on 20/05/2025 :We are discussing with the consulting team; they will already be preparing a drawing for the fire protection system. We will complete the work in RSC Timeline. | Nov 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 6 Months | In Progress
Initial Inspection |  | 3 | Installed fire doors are not functional properly due to non-functional door accessories including door coordinators, closing device, magnetic door holders and panic hardwares. Credible certifications required. | Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. The clearance under the bottom of a fire door shall be a maximum of 3⁄4 in. (19 mm). | Update on 20/05/2025 :The installed fire doors are properly functional. Door accessories including door adjusters, closing devices, magnetic door holders and panic hardware are functional. Credible certifications have been collected. We will complete the work in RSC Timeline. | Jul 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 2 Months | In Progress
Initial Inspection |  | 4 | The exit stair enclosures are not separated from work areas and other spaces on each floor by fire-rated construction. Location: Warehouse Rack Shed (Exit stairs from mezzanine floors). | The exit stair enclosure shall be provided with a minimum 1-hr fire resistance rating for buildings with 3 or fewer stories and a minimum of 2- hr. fire resistance rating for buildings 4 or more stories. Provide 1-hr. fire rated door and seal all penetrations and openings by 1 hr. fire rated fire rated barrier construction for building with 3 or fewer stories. Provide 1.5 hr. fire rated door and seal all penetrations and openings by 2 hr. fire rated fire rated barrier construction for building with 4 or more stories in accordance with section 6.3.1.2 of RSC Technical Guidelines (Standard)¹ V1.0. Provide a fire-resistive rated assembly between the exterior exit stairs and the building up to 10 ft. beyond the end of the stair to achieve the required separation. The rated assembly shall be approved and/or designed by a qualified fire protection engineer. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Update on 20/05/2025 : We appoint a consultant to design the exterior exit stairs with required separation as your guideline. after design complete, we will send it to RSC for review and approve. after approve we will separation the stair with fire-resistive rated. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 5 | A catwalk (deck) has been constructed on the high-rack storage, and the area of the intermediate deck creates a separate floor, as the size of the decks exceeds 33% of the total floor area, requiring fire-rated separation. Location: Warehouse Rack Shed. | Remove the catwalk of the intermediate deck. Or , The floor must adhere to the RSC building standards and BNBC 2006 regulations regarding fire rated construction and egress features. | Update on 20/05/2025 : We appoint a consultant to review the floor with RSC building standards and BNBC 2006 regulations regarding fire rated construction.He has review and after review we will arrange required materials to complete floor fire rated seperation. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 6 | The available Travel distance (142 ft) exceeds the maximum allowable limit where only a single means of exit has been provided and does not meet the requirements of Section 6.13 of RSC Technical Guidelines (Standard). . Location: 1st floor of 2-storied female toilet building. | Reconfigure the egress arrangement or provide additional exits so that the travel distance shall not exceed 45 m. or, Provide a standpipe system in accordance with the RSC Technical Guidelines (Standard) along with the automatic fire detection system, and portable fire extinguishers to increase the travel distance limitations for G2 (RMG factories) to 60 m (200 ft). or, Provide a complete automatic sprinkler system in accordance with the RSC Technical Guidelines (Standard) along with the automatic fire alarm system, and portable fire extinguishers to increase the travel distance limitations for G2 (RMG factories) to 122 m (400 ft). | Update on 20/05/2025 : We appoint a consultant to design a stair on north side and then we will provide additional exits so that the travel distance shall not exceed 45 m. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 7 | The available Dead-end corridor distance (100 ft) exceeds the maximum allowable limit. Location: 1st floor of 2-storied female toilet building. | Reconfigure the egress arrangement to reduce the maximum dead- end corridor to meet Table 6.13.3 of RSC Technical Guidelines (Standard). | Update on 20/05/2025 : we will provide a secondary exists which will remove dead-end corridor system. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 8 | Boiler shed is not separated from other occupancies by fire rated construction. Location: boiler shed and multipurpose shed. | Boilers or other heat producing equipment shall be separated from other occupancies by a minimum 1-hr fire rated construction (wall, floor, slab etc.). Seal all penetrations and openings (door, window etc.) should be protected by 0.75-hr (45 min) fire rated materials to maintain the fire separation if required. All exhaust systems shall discharge to the exterior of the building in a safe location. Or Relocate it to exterior of the building and maintain a minimum 3m (10 ft.) spatial separation distance from the building. Boiler room separation shall meet section 3.4.2.1.2 of RSC Technical Guideline (Standard). | Update on 20/05/2025 : we will Seal all penetrations and openings fire rated materials to maintain the fire separation protected by 0.75-hr (45 min) . we will provide all exhaust system to discharge to the exterior of the building in a safe location. Update on 20/05/2025 : We will Relocate it to exterior of the building which maintain a minimum 3m (10 ft.) spatial separation distance from the building. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 9 | Non-compliant doors (Sliding type doors) are provided along with the means of egress at several locations. Location: Multipurpose shed. | Replace all collapsible/sliding/shutter type doors & gates by the side-hinged swinging type doors in accordance with section 6.8.1 of RSC Technical Guidelines (Standard)¹ V1.0. All doors in a means of egress shall be of the side-hinged swinging type. Roll--down and sliding gates and shutters shall not be allowed. Doors serving an occupant load of more than 50 shall swing in the direction of egress travel. | Update on 20/05/2025 : We will replace the sliding door to Hinged swing door. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 10 | Stair width is found less than 60 in. (found 31 in.) from high rack deck. Location: Warehouse Rack Shed. | Stairs shall have a minimum clear width of 60 in. for all industrial occupancies as per RSC Technical Guideline (Standard) section of 6.5.6. | Update on 20/05/2025 : We contact with a consultant for guideline to modify the stair and make width 60 inch in RSC standard. We will complete the work in RSC Timeline. | Aug 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 3 Months | In Progress
Initial Inspection |  | 11 | Aisles marking was not provided on several areas. locations: Multipurpose shed. | Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 in.) in accordance with section 6.5.1 of RSC Technical Guidelines (Standard)¹ V1.0. | Update on 20/05/2025 : Aisles have provide the area with a clear width of 36 inch. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 12 | Updated evacuation map is not posted at the entrance of all exit stairs on each floors. | Update the fire evacuation map and shall be posted at the entrance to each exit stair in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 13.3. | Update on 20/05/2025 : we contact with the print supplier to correction the evacuation plan. after received we will post it. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 13 | Building did not have updated occupant load signs at all required locations on each floors | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.4.4. | Update on 20/05/2025 : we have order the occupant load sign and after receive we will post it every exit point. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 14 | The directional signs are not provided where there is a change in direction and where the continuation of the egress path is not obvious. | Illuminated directional signs shall be provided where there is a change in the direction for the path of travel and the direction to an exit is not obvious in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.11.3. | Update on 20/05/2025 : we have order the Illuminated directional signs and after receive we will hang it. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 15 | illuminated Exit signs are not provided at all exits. | Lighted exit signs shall be placed at entrance to an exit. Additional directional exit signs shall be placed throughout the facility anywhere the continuation of the egress is not obvious. Lighted exit signs shall be provided with either battery backup or uninterruptable power supply systems and shall be continuously illuminated at all times. Exit Sign shall provide in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 6.1 | Update on 20/05/2025 : we have order the illuminated Exit signs and after receive we will hang it in all exit point. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 16 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: Each floors. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. Illumination on means of egress shall meet in accordance with RSC Technical Guidelines (Standard)¹ V1.0 Section 10.12.2. | Update on 20/05/2025 : we have checked the area light lux and order required light. we will provide required light at the located area. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 17 | Inspection, testing, and maintenance for the exit sign and emergency lighting system were not in accordance with the RSC Technical Guidelines (Standard). | Inspect, test and maintain the exit sign and emergency lighting system in the accordance with the RSC Technical Guidelines (Standard)¹ V1.0. Keep written records on-site. | Update on 20/05/2025 We have Inspection, testing and maintenance exit sign and emergency lighting system will be performed in accordance with RSC Technical Guidelines (Standard)..Within 1 month (after installation) We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress
Initial Inspection |  | 18 | Automatic fire alarm & detection system installation requires detailed review to confirm compliance with NFPA-72 and RSC Technical Guidelines (Standard). | Submit the fire alarm and detection system design to RSC for review. Once the design is reviewed, install and modify the fire detection and alarm system throughout the building in accordance with review comment, RSC Technical Guidelines (Standard) and NFPA 72. After installation the owner shall conduct internal testing and commissioning and then contact the RSC for witness of final acceptance testing. | Update on 20/05/2025 We are discussing with the consulting team; they will already be preparing a drawing for the fire Automatic fire alarm & detection system.Once the design review is complete, we will install and modify the fire detection and alarm system throughout the building in accordance with the review comments, RSC Technical Guidelines (Standards), and NFPA 72. We will complete the work in RSC Timeline. | Nov 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Design within 2 month and modification/ installation with 4 months | In Progress
Initial Inspection |  | 19 | Inspection, testing and maintenance for the fire alarm system is not in accordance with NFPA 72 and The RSC Technical Guidelines (Standard). | Inspect, test and maintain the fire alarm system and keep written records on-site, in accordance with NFPA 72 and RSC Technical Guidelines (Standard)¹ V1.0.s | Update on 20/05/2025 : Inspection, testing and maintenance fire alarm system will be performed in accordance with NFPA 72.Within 1 month (after installation) We will complete the work in RSC Timeline. | Dec 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 20 | The multistoried Warehouse Rack Shed building has an occupied floor height (41 feet 6 inch) greater than 10 meters (33 feet). So that standpipe system is required throughout the building. Fire Pump and Standpipe system installation requires detailed review to confirm compliance with NFPA 13, 14, 20, 22, 24 & RSC Technical Guidelines (Standard). | A standpipe system shall be installed in buildings with the highest occupiable floor 10 m (33 ft.) above grade or more to meet section 5.4.2 of RSC Technical Guideline (Standard). If the building is protected throughout by an approved automatic sprinkler system a class I system shall be permitted.) Installation of the Standpipe system shall be in accordance with RSC Technical Guidelines (Standard)¹ V1.0. section 5.4 and NFPA 14. Submit the standpipe system drawing to RSC for review. Once reviewed, install or modify the standpipe system throughout the building in accordance with RSC Technical Guidelines (Standard)¹ V1.0. and NFPA 14,20,22 and 24. After installation the owner shall contact the RSC for witness of conducting the final acceptance testing of the standpipe system. | Update on 20/05/2025 : we already contact with a consultant for design. after receive the design we will send it to RSC on mail for review and approval. after approval we will complete the work with RSC standard. We will complete the work in RSC Timeline. | Nov 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Design within 2 month and modification/ installation with 4 months | In Progress
Initial Inspection |  | 21 | Inspection, testing and maintenance of the fire pump system is not in accordance with NFPA 25. | Inspect, test and maintain the fire pump system and keep written records on-site, in accordance with NFPA 25 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Update on 20/05/2025 : Inspection, testing and maintenance of fire pump systems will be performed in accordance with NFPA 25.Within 1 month (after installation) We will complete the work in RSC Timeline. | Dec 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 22 | Inspection, testing and maintenance of the standpipe system is not in accordance with NFPA 25. | Inspect, test and maintain the standpipe system and keep written records on-site, in accordance with NFPA 25 and RSC Technical Guidelines (Standard)¹ V1.0.s. | Update on 20/05/2025 : Inspection, testing and maintenance of standpipe systems will be performed in accordance with NFPA 25.Within 1 month (after installation) We will complete the work in RSC Timeline. | Dec 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 month (after installation) | In Progress
Initial Inspection |  | 23 | Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and RSC Technical Guidelines (Standard). | Update on 20/05/2025 :We will prepare for the inspection, testing, and maintenance of portable fire extinguishers in accordance with NFPA 10. We will complete the work in RSC Timeline. | Jun 20 2025 | CAP reviewed on 29-May-2025. Complete the remediation within the given timeline RPO Comments on 10 Aug 25: Due to insuffient evidence the issue will remain in progress. | Within 1 Month | In Progress

## Electrical
Date
10-Nov-2025 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | ULTIMATE FASHIONS LIMITED (EXTENSION), South Gouripur, Dhaka, Dhaka
Date of Inspection |  | 2025-02-20
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Field information has no/less reflection in existing SLD. | As-built Electrical Single Line Diagram (SLD) must be prepared by a qualified engineer, including all essential details of the electrical system. This diagram must be reviewed and approved by the RSC. The accepted SLD needs to be implemented at the factory. All cables, all circuits, all terminals, all equipment are required to be identified as per the accepted Single line diagram. |  | Nov 20 2025 | On 29/10/2025: Corrected. | 6 Months | Corrected
Initial Inspection |  | 2 | Lightning Protection System (LPS) is not maintained properly. Issues include air terminal bent, loose or disconnected conductors, rusty equipment etc. | Regularly scheduled maintenance procedures must be conducted to ensure the continued effectiveness and reliability of the Lightning Protection System (LPS), preserving its ability to protect against lightning strikes. | Corrected. | Aug 20 2025 | On 29/10/2025: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Insulation resistance test is not performed for all electrical power cables. | Insulation resistance testing of all cables (excluding those less than 25 sq.mm) must be conducted once every two years and documented. This testing may require power shutdown to ensure accurate results and safety. |  | Jun 20 2025 | On 29/10/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Thermography scanning report is not available for all panels boards. | Thermography survey of the entire electrical system must be conducted and documented by bi-annual, including real-time and scanned images with recommendations for corrective actions. This helps identify overheating, loose connections, and safety hazards, preventing equipment failure and reducing downtime. |  | Jun 20 2025 | On 29/10/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Panel/Distribution boxes are inaccessible or cannot be opened to perform any maintenance work or inadequate clearance. | Each electrical distribution board or panel must be easily accessible, maintaining a minimum working clearance of 1 meter (or equal to the width of the board/panel, whichever is greater). The panel's height must not be exceed 2 meters, and the bottom must be at least 0.45 meters above from the floor or working platform (for wall-mount panel). The board/panel door must open at least 90 degrees to ensure safe and efficient operation and maintenance. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 6 | Multiple cables from different electrical consumers are terminated at circuit breaker terminals or busbars. | Each electrical circuit must be terminated at a single circuit breaker terminal or busbar to ensure distribution and protection within the electrical system. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 7 | Loop connection has been used powering multiple circuits through circuit breakers. | No loop connections are allowed. Each cable must be terminated with a single cable lug at each terminal. Combo bus bars are permitted if the incoming cable size meets the rated capacity. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 8 | No/Inadequate rubber (insulation) mat at the working area of distribution board/panel. | Electrical insulation, with a thickness of at least 3 mm for rubber mats, must be provided at the working area of each electrical installation. Length of the mat shall be equal to 1 meter or the width of the board/panel, whichever is greater. This includes areas of LT panels, MDBs, DBs, SDBs, and other manually operated machinery to ensure safety and prevent electrical hazards. | Corrected. | Jun 20 2025 | On 29/10/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 9 | Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor cables must be covered, if required. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 10 | Wiring or extensions connecting equipment/ devices are laid on floors without protection, using flexible PVC. | Run the cable connections to machines/equipment through trenches covered with checkered plates or within rigid conduits/cable trays and supports to prevent external damage. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 11 | Outdoor Cable is not covered to protect from the weather effects. | All power cables exposed to weather shall have cover unless it is specified for outdoor wiring. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 12 | Exposed terminal joint or unsafe wiring on outdoor wiring. | All unsafe wiring shall be removed. Cable terminal joint using busbar shall be done within enclosure with proper earthing. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 13 | Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine, accessible to users/operators, must be equipped with an earth connection. Cable selection should be based on the protective device's response and the power demand of the circuit. | Corrected. | Jun 20 2025 | On 29/10/2025: Corrected. | 1 Month | Corrected
Initial Inspection |  | 14 | Power sockets are kept on floor without support. | Power sockets must be securely installed on rigid supports or bases, positioned at a minimum height of 200mm above the floor level. | Corrected. | Jul 20 2025 | On 29/10/2025: Corrected. | 2 Months | Corrected
Initial Inspection |  | 15 | Uncovered cable used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Corrected. | Aug 20 2025 | On 29/10/2025: Corrected. GI pipe used to remediate this issue. | 3 Months | Corrected

## Boiler
Date
10-Nov-2025 | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address
Date of Inspection
Finance Plan Agreed | Yes