## Structural
Date
19-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Unique Designers, Unique Designers Ltd, Kalemshar, K.B. Bazar,, Gazipur, Gazipur
Date of Inspection |  | 2014-05-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | FoS were calculated using the minimum concrete material strength in the Alliance Standard Protocol (2370 psi). The FoS of Central Column is 2.18(Safe),for corner column is 3.30(Safe)and for edge column 1.75(Needs Evaluation) noted to have exceeded the acceptable limit. Immediate reduction of load required. | Engage a qualified structural engineer and carry out structural assessment to identify what remedial action is appropriate, which may include retrofitting.Reduction of load is required before any other remedial action is undertaken based on detailed structural assessment. | Corrected | Jul 20 2017 | On 14/03/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: DEA of the factory was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Factory had completed all remediation work as per re-accepted DEA. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. | Aug 21 2014 | Corrected
Initial Inspection |  | 2 | Structural assessments are provided only for gravity load, but details of engineering analysis for wind load and earthquake have not been done. | Details of engineering analysis for wind load and earthquake have to be done. | Corrected | Jul 20 2017 | On 14/03/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: DEA of the factory was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. | Aug 21 2014 | Corrected
Initial Inspection |  | 3 | Credible structural document does not indicate general conformance with BNBC 2006 or other comparable applicable international model building code. | Engage a qualified structural engineer to develop the required documents to confirm the structural integrity of the buildings. Documents must comply with Alliance Standard Part 8 Section 8.19 and 8.20 | Corrected | Jul 20 2017 | On 14/03/2018: As-built drawings are prepared as a part of DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: As built drawings have been prepared as part of DEA which was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. During inspection no further mismatch was found. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. | Aug 21 2014 | Corrected
Initial Inspection |  | 4 | The lateral load path is not apparent, and further information is required for understanding the redundancy. | Have a qualified structural engineer complete further analysis of the structure and develop a remediation plan if required. Design report is to be prepared and submitted by the design engineer. | Corrected | Jul 20 2017 | On 14/03/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: DEA of the factory was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Factory had completed all remediation work as per re-accepted DEA. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. | Aug 21 2014 | Corrected
Initial Inspection |  | 5 | Structural documents are available except for the design report. | Have a qualified structural engineer prepare design report as per BNBC. | Corrected | Jul 20 2017 | On 14/03/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: DEA of the factory was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. However a new structure named Wastage shed was found in the South-East corner of the Production Building. As-built drawing of the shed was available and found satisfactory with onsite condition. | Aug 21 2014 | Corrected
Initial Inspection |  | 6 | Standing water was found on the roof. | Under guidance from a qualified structural engineer, address all areas of needed maintenance by correcting the identified issues. | Corrected | Jul 20 2017 | On 14/03/2018: Roof drainage system has been improved. During inspection, standing water wasn’t found on roof. On 25/09/2018: This issue has been corrected as per 1st follow up inspection. No standing water was found on the roof top. On 02-Jan-2023: Corrected from previous inspection. During inspection no water ponding was observed. On 03-Mar-2024: Corrected previously. During inspection, no water ponding was observed on roof. | Aug 21 2014 | Corrected
Initial Inspection |  | 7 | There are no provisions made at the roof level for the concentrated loads caused by 5 UPVC water tanks. No other concentrated loads that would cause over stressing of the structure were observed in the building. | Engage a qualified structural engineer to confirm and document that provisions have been made to accommodate concentrated loads. If provisions have not been made, have a qualified structural engineer develop a remediation plan. | Corrected | Jul 20 2017 | On 14/03/2018: Water tanks were found as per accepted load plan. On 25/09/2018: This issue has been corrected as per 1st follow up inspection. Water tanks were found as per accepted load plan. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Factory had completed all remediation work as per re-accepted DEA. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. During inspection, 4 UPVC water tanks (2X2000 litre & 2X1500 litre) were found on roof. | Aug 21 2014 | Corrected
Initial Inspection |  | 8 | Documentation cannot be provided that the building is compliant with the requirements for wind loading and storm surge loadings as detailed in BNBC Part 6 Section 1.5.3. | Engage a qualified structural engineer to confirm satisfactory structural performance of the buildings under wind loading. | Corrected | Jul 20 2017 | On 14/03/2018: This issue has been covered in DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in between as-built drawings and on-site condition. Factory is required to revise the documents as per DEA verification report and submit to Alliance within mentioned time-line. On 25/09/2018: This issue has been covered in DEA. DEA of the factory was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. On 02-Jan-2023: Corrected from previous inspection. This issue had been covered in DEA which had been re-accepted from Alliance on 27/09/2018. Also, factory got No Color Certificate from Accord on 25 Feb 2019. On 03-Mar-2024: Corrected previously. | Aug 21 2014 | Corrected
Initial Inspection |  | 9 | Plastic water tanks resting on the rooftop are not anchored or braced to adequately resist earthquake forces. | Adequately anchor and brace all non-structural elements to resist earthquake forces to comply with the BNBC and Alliance Standard. | Corrected | Jul 20 2017 | On 14/03/2018: Water tanks have been braced and non-structural elements have been anchored. On 25/09/2018: This issue has been corrected as per 1st follow up inspection. Water tanks have been braced and non-structural elements have been anchored. On 02-Jan-2023: Corrected from previous inspection. During inspection all non structural elements were found anchored and braced. On 03-Mar-2024: Corrected previously. During inspection, all non-structural elements (plastic water tank, racks) were found anchored. | Oct 2 2014 | Corrected
Initial Inspection |  | 10 | There is no program available to manage floor and roof live loads. | Develop a program to ensure that all live loads for which a floor/roof has been designed will not be exceeded. The designated Load Manager shall oversee this program and ensure it is enforced. | Corrected | Jul 20 2017 | On 14/03/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in as-built drawings. Proper load management program was not found during inspection. However, load plans were found posted on each floor and floor loading was found within the allowable limit. On 25/09/2018: Load plan has been prepared as part of DEA which was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. During inspection no further mismatch was found. As per recommendation of accepted DEA, factory building required column strengthening. Factory completed all remediation works. Factory is now following final load plan (allowable 3kPa). Load plan was found posted on each floor plates. On 02-Jan-2023: Corrected from previous inspection. Load plan had been produced and accepted as a part of DEA. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (3 kPa). On 03-Mar-2024: Corrected previously. During inspection, load plans were found posted at each floor and loading was found below accepted load limit (3 kPa). | Aug 7 2014 | Corrected
Initial Inspection |  | 11 | Factory Load manager or designated representative is not available. | Designate a representative as the Factory Load Manager. The Factory Owner shall ensure that at least one individual, the Factory Load Manager who is located onsite full time at the factory, is trained in calculating operational load characteristics of the specific factory. The Factory Load Manager shall serve as an ongoing resource to RMG vendors and be responsible to ensure that the factory operational loads do not at any time exceed the factory floor loading limits as described on the Floor Loading Plans. | Corrected | Jul 20 2017 | On 14/03/2018: Load manager has been appointed. On 25/09/2018: This issue has been corrected as per 1st follow up inspection. On 02-Jan-2023: Corrected from previous inspection. Load manager had been appointed and he was present during inspection. On 03-Mar-2024: Corrected previously. During inspection, load manager was present onsite. | Aug 7 2014 | Corrected
Initial Inspection |  | 12 | No load plans have been prepared for each floor documenting the actual maximum operational loading that is intended or allowable on each floor. | Have a qualified structural engineer develop Floor Loading Plans per the requirements of Part 8 Section 8.20.5.3 | Corrected | Jul 20 2017 | On 14/03/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance on October 23, 2016. During inspection some discrepancies were found in as-built drawings. Proper load management program was not found during inspection. However, load plans were found posted on each floor and floor loading was found within the allowable limit. On 25/09/2018: Load plan has been prepared as part of DEA which was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. During inspection no further mismatch was found. As per recommendation of accepted DEA, factory building required column strengthening. Factory completed all remediation works. Factory is now following final load plan (allowable 3kPa). On 02-Jan-2023: Corrected from previous inspection. Load plan had been produced and re-accepted from Alliance 27/09/2018. During inspection accepted load plan was found posted at every floor and live load was found below the allowable limit (3 kPa). On 03-Mar-2024: Corrected previously. During inspection, load plans were found posted at each floor and loading was found below accepted load limit (3 kPa). | Aug 21 2014 | Corrected
Initial Inspection |  | 13 | Floor Load Plans are not posted as required. | Have a qualified structural engineer prepare load plans including the information required in Section 8.20 of the Alliance Standard. | Corrected | Jul 20 2017 | On 14/03/2018: Load plans are prepared as part of DEA. DEA of this factory had been reviewed and accepted by Alliance. During inspection, load plan was found posted on each floor and floor loading was within allowable limit. Because of discrepancies, factory is required to submit revised DEA to Alliance. Factory shall post the final load plan as per revised DEA after getting re-acceptance form Alliance. On 25/09/2018: Load plan has been prepared as part of DEA which was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. During inspection no further mismatch was found. As per recommendation of accepted DEA, factory building required column strengthening. Factory completed all remediation works. Factory is now following final load plan (allowable 3kPa). On 02-Jan-2023: Corrected from previous inspection. Load plan had been produced and re-accepted from Alliance 27/09/2018. On 03-Mar-2024: Corrected previously. During inspection, load plans were found posted at each floor and loading was found below accepted load limit (3 kPa). | Aug 21 2014 | Corrected
Initial Inspection |  | 14 | Storage of work materials and work products are not marked to indicate the acceptable loading limit, and each floor's load plan is not available on the floor. | Provide signage or the appropriate markings at all areas used for storage to indicate the acceptable loading limits detailed in the Load Plan. | Corrected | Jul 20 2017 | On 14/03/2018: Signage and load limit information has been provided on storage area as per previously accepted load plan. Because of discrepancies, factory is required to submit revised DEA to Alliance. Factory shall update the signage and load limit information as per revised DEA after getting re-acceptance form Alliance. On 25/09/2018: Load plan has been prepared as part of DEA which was accepted from Alliance on 23/10/2016. Revising the discrepancies found during verification inspection on 14/03/2018, factory re-submitted the DEA to BUET. Factory has received approval from BUET and sent the approved documents to Alliance. Alliance reaccepted the revised DEA documents on 27/09/2018. During inspection no further mismatch was found. As per recommendation of accepted DEA, factory building required column strengthening. Factory completed all remediation works. Factory is now following final load plan (allowable 3kPa). Load plan was found posted on all floor plates. Load markings were provided as per allowable load limit. On 02-Jan-2023: Corrected from previous inspection. During inspection load height marking was observed at storage areas and live load was found below the load marking (3 kPa). On 03-Mar-2024: Corrected previously. During inspection, maximum load height marking was found at storage area and loading was found below that marking. | Jul 21 2014 | Corrected
Initial Inspection |  | 15 | Cracks have been observed in the exterior façade. | Engage a qualified structural engineer provide further analysis of the identified cracks to determine the appropriate course of corrective action. | Corrected | Jul 20 2017 | On 14/03/2018: Cracks have been repaired in the exterior façade. On 25/09/2018: This issue has been corrected as per 1st follow up inspection. Cracks were repaired. On 02-Jan-2023: Corrected from previous inspection. Crack had been repaired long ago and during inspection no further crack was observed. On 03-Mar-2024: Corrected previously. During inspection, no further crack was observed. | Aug 21 2014 | Corrected
Initial Inspection |  | 16 | Certificates of Occupancy are not available for review. | Occupancy certificate needs to be collected from the proper authority. | Corrected | Jul 20 2017 | On 14/03/2018: Not applicable as per Alliance report. On 25/09/2018: N/A. On 02-Jan-2023: Corrected from previous inspection. On 03-Mar-2024: N/A. | Aug 21 2014 | Corrected
Follow Up Inspection |  | 17 | New finding-1: Column Cracks at Generator shed | Building engineer is required to investigate the cause of cracks and take remedial measures. | Corrected | Oct 4 2018 | On 14/03/2018: Cracks found on column at generator room. Building engineer is required to investigate the cause of cracks and take remedial measures. On 25/09/2018: Cracks were found repaired. Factory has prepared a crack investigation report stating the reason of cracks and recommending required remediation. On 02-Jan-2023: Corrected from previous inspection. Crack had been repaired as per investigation report and during inspection no further crack was observed. On 03-Mar-2024: Corrected previously. During inspection, no further crack was observed. | Immediately | Corrected
Follow Up Inspection |  | 18 | New finding-2: Significant vibration observed on 1st floor washing area (Production Building). | Building engineer is required to investigate the area and propose suitable measure. | Corrected | Feb 14 2023 | On 02-Jan-2023: Significant vibration observed on 1st floor washing area (Production Building). Building engineer is required to investigate the area and propose suitable measure. On 03-Mar-2024: As per recommendation of investigation report factory introduce rubber pad below the machines and during inspection, no vibration was observed. | (within 6 weeks) | Corrected
Follow Up Inspection |  | 19 | New finding-3: Crack found on beam surface at single storied platform (Chemical Mixing Area). | The factory must immediately engage a consultant to investigate the cracks. Any safety measures, if required as suggested by the consultant, must be taken immediately to ensure safety. The investigation report along with the repair methodology must be submitted to RSC. | Corrected | Jan 10 2023 | On 02-Jan-2023: Crack found on beam surface at single storied platform (Chemical Mixing Area). The factory must immediately engage a consultant to investigate the cracks. Any safety measures, if required as suggested by the consultant, must be taken immediately to ensure safety. The investigation report along with the repair methodology must be submitted to RSC. On 03-Mar-2024: Factory has produced crack investigation report which was reviewed and accepted by RSC on 29-Jan-2023. As per recommendation of the report, factory has demolished RC roof and constructed steel roof. | (Immediate – Now) | Corrected
Follow Up Inspection |  | 20 | New finding-3: Crack found on beam surface at single storied platform (Chemical Mixing Area). | The remediation work must be completed as per investigation report. | Corrected | Feb 14 2023 | On 02-Jan-2023: The remediation work must be completed as per investigation report. On 03-Mar-2024: Factory has produced crack investigation report which was reviewed and accepted by RSC on 29-Jan-2023. As per recommendation of the report, factory has demolished RC roof and constructed steel roof. | (within 6 weeks) | Corrected

## Fire
Date
19-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Unique Designers, Unique Designers Ltd, Kalemshar, K.B. Bazar,, Gazipur, Gazipur
Date of Inspection |  | 2014-05-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Some aisles on 4th floor of main building were found obstructed by column. | Keep aisles free and unobstructed at all times. Aisles shall be provided with a minimum unobstructed clear-width of 0.9 m (36 inches). | Corrected | Mar 30 2016 | On 18-01-16: No action has been taken yet. On 30-03-16: Corrected. On 24-07-16: Corrected. Aisles were unobstructed. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Sep 1 2014 | Corrected
Initial Inspection |  | 2 | Door widths are more than 0.8m, but all doors along the path of egress (i.e. doors leading to staircases) in buildings are not fire doors. | Provide 1 hr fire protective opening assemblies in 1 hr rated exit enclosures. Provide 1.5 hr fire protective opening assemblies in 2 hr rated exit enclosures. Exits connecting three or fewer stories shall be enclosed with a minimum 1-hr fire-resistance rating. Exits connecting four or more stories shall be enclosed with a minimum 2-hr fire-resistance rating. Exits shall be enclosed with the same fire-resistance rating as the floor penetrated but will not need to exceed 2 hr. | Corrected | Aug 16 2017 | On 25/09/2018: S-E stair is not enclosed/separated form other occupancies at ground level and N-E stair is not separated from newly established transformer room and other areas at ground floor. On 24/11/2018: Fire doors were not fully functional. Door coordinators, closers shall be maintained properly. On 17/09/2019: Closer shall be functional. All seal need to be with FD and check list shall be prepared properly On 29/04/2024: Corrected. Installed fire doors were found properly functional during inspection. | Sep 1 2014 | Corrected
Initial Inspection |  | 3 | There are collapsible doors, steel rolling shutter doors, & wooden swinging doors with locking arrangements at some egress locations. | Replace all collapsible, sliding, roll-down gates and shutters in means of egress with side-hinged swinging type doors of proper width and rating in accordance with Alliance Standard. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Replaced with doors with the correct swing. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Sep 1 2014 | Corrected
Initial Inspection |  | 4 | On ground floor, there are 7 exits including 4 stairs (serving the upper levels). 3 out of 4 stairs lead directly to the street and southeast stair discharges through an egress court between generator shed and production building which is not fire rated. From the west side of ground floor 3 exits discharge through an egress court which is not fire rated. Among them 2 exits pass beside the boiler and generator room on west side, one exit (southwest) passes beside the utility shed. Also all the three exit discharge passes between generator shed and production building on east side which is not fire rated. | Provide rated exit passageway i.e. protected path of egress from the exit enclosure to the public way. The rating of the exit passageway is to be equal to fire rating requirement of the exit that is being served and shall not be less than 1 hr fire-resistance rated. | Corrected | Jan 31 2017 | On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. Note: The egress court shall be kept clear of any kind of obstruction. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected based on previous follow ups. On 24/11/2018: Corrected based on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected as per previously. The factory need to separated childcare room & doctor room from exit enclosure -4 | Sep 1 2014 | Corrected
Initial Inspection |  | 5 | A class III standpipe system needs to be installed throughout the building at required stairwells as per Alliance Standards, but only a class II stand pipe system is installed in the main building. At all floors except roof, 4 class-II standpipe hose connections (40 mm) are installed. At roof, there are 2 hose connections. At roof, hose pressure was less than 4.5 bar. Hose size and pressure are not sufficient and nozzle is fixed type. | Install a NFPA 14-compliant standpipe system at required locations designed by a qualified fire protection engineer. All standpipe system installations and hydraulic calculations shall be reviewed by the Alliance prior to commencement of installation. | We already completed all relevant work & sent to RSC for review & waiting for verification. | Dec 31 2016 | On 25/09/2018: Reportedly system is ready for T&C however control valves are not supervised yet. On 24/11/2018: T&C was conducted by Accord. Few deficiencies were observed. a) Pump performance test couldn't be conducted as the diesel pump failed to give 150% of its rated output. b) Improper pressure setup observed. c) Tank capacity not found and found inadequate. d) Inadequate reservoir observed. e) Improper drainage and ventilation system. f) Reservoir shall be in auto refill condition. g) Vortex plate shall be used. h) Required pressure was not found at remote riser. i) In detail reservoir drawing shall be provided. On 17/09/2019: In progress. T&C needed. On 29/04/2024: In progress observed. The factory has completed some modification work & other modification work is going as per last Pre-T&CVI. After complete the modification work, factory need to apply formal T&C to RSC. On 21/01/2024: Pre T&C found that the system is not corrected. See the detailed Pre T&C report. RPO Comments: On 19-May-2026 the T&CVI documents are pending to be submitted to RSC. | Sep 1 2014 | In Progress
Initial Inspection |  | 6 | There are four stairs in the production building. Fire doors are installed at stairs of south and north sides on all floors except 5th floor, which is being used as an occupied roof. Certificates of fire doors are not available. Fire doors are not installed at the other two stairs on any floor of the building. There are openings in exterior wall of production area within 10 ft of a staircase which has no wall on two sides. | Provide 2 hr fire-resistive rated construction barriers at exit enclosures. Fit doors that swing in the direction of egress, side-swinging, self-closing, non-lockable fire doors of 1.5 hr rating in all stairwell enclosures. Consult a qualified fire protection engineer to design the required rated construction barriers. | Corrected | Jan 31 2017 | On 24-07-16: In progress. Factory has begun civil work and installed fire doors at their exits. Fire doors were held open with external objects. If doors are to be held open for functional reasons, Factory shall install electromagnetic door holders interfaced with the FACP. Double doors shall have proper door coordination. On 12/03/2017: In progress. On 18-6-2017: Not completed yet. Several fire doors require extensive maintenance. Door hold open devices shall be automated to release when alarm is triggered. Staircase enclosure shall be separated from all areas. On 22.02.2018: Not completed yet. Door co-ordinator was not working properly. On 25/09/2018: Repeated finding. Refer to issue 2. On 24/11/2018: Corrected as per previous follow-up. Refer to issue 2. On 17/09/2019: Corrected as per previous follow-up. Refer to issue 2. On 29/04/2024: Corrected. Installed fire doors were found functional during inspection. | Sep 1 2014 | Corrected
Initial Inspection |  | 7 | A fire pump is available, but it does not comply with the requirements of Alliance Standards. Hydraulic calculation for installed standpipe system is not available. The pump is not connected to an alternative power source. The capacity of the water reservoir is not sufficient. | Upgrade current pump or install a pump dedicated for fire protection following the requirements of NFPA 20. Fire pump installation is to be tested for final acceptance in presence of Alliance and a final inspection shall be conducted by the Alliance prior to final acceptance. Acceptance testing of the installation shall be in accordance with NFPA 25 testing requirements. Documentation of all testing shall be submitted to the Alliance for review prior to final acceptance. | We already completed all relevant work & sent to RSC for review & waiting for verification. | Dec 31 2016 | On 25/09/2018: Reportedly system is ready for T&C however control valves are not supervised yet. On 24/11/2018: T&C was conducted by Accord. Few deficiencies were observed. a) Pump performance test couldn't be conducted as the diesel pump failed to give 150% of its rated output. b) Improper pressure setup observed. c) Tank capacity not found and found inadequate. d) Inadequate reservoir observed. e) Improper drainage and ventilation system. f) Reservoir shall be in auto refill condition. g) Vortex plate shall be used. h) Required pressure was not found at remote riser. i) In detail reservoir drawing shall be provided. On 17/09/2019: T&C needed. On 29/04/2024: In progress observed. The factory has completed some modification work & other modification work is going as per last Pre-T&CVI. After complete the modification work, factory need to apply formal T&C to RSC. On 21/01/2024: Pre T&C found that the system is not corrected. See the detailed Pre T&C report. RPO Comments: On 19-May-2026 the T&CVI documents are pending to be submitted to RSC. | Jul 15 2014 | In Progress
Initial Inspection |  | 8 | Fire doors are installed at two staircases (south and north stairs) from ground floor to 4th floor but are not installed at 5th floor, which is being used as an occupied roof. Certificates for fire doors are not available. At other two stairs (south-middle and north-middle stairs), fire doors are not installed on any floor. Openings in rated walls of boiler room, generator room and chemical store at ground floor of main building are not fire protected. | Install fire rated doors and windows or fill in unprotected openings with fire resistive rated assemblies. | Corrected | Jan 31 2017 | On 18-6-2017: Not completed yet. Several fire doors require extensive maintenance. Door hold open device shall be au mated to release when alarm is triggered. On 22.02.2018: Not completed yet. Door co-ordinator was not working properly. On 25/09/2018: Repeated finding. Refer to issue 2. On 24/11/2018: Corrected as per previous follow-up. Refer to issue 2. On 17/09/2019: Corrected as on previous follow ups. Refer to issue no 2. On 29/04/2024: Corrected. | Sep 1 2014 | Corrected
Initial Inspection |  | 9 | On ground floor 3 out of 4 stairs lead directly to the street and southeast stair discharges through an egress court (7 ft wide) between generator shed and production building which is not fire rated. | Provide walls having 1‐hr fire resistance rated construction for a distance of 3050 mm (10 ft) above the floor of the court. | Corrected | Mar 30 2016 | On 18-01-16: Partially corrected. On 30-03-16: Corrected. Factory have sealed all the penetrations up to 10-ft of height of the shed building. On 24-07-16: Corrected. Sealed. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Dec 2 2014 | Corrected
Initial Inspection |  | 10 | On 1st floor of main building, exit access corridor is partly a brick wall partition with an aluminum and wooden side swinging door, which is not 1 hour fire rated. | Provide fire-resistive rated assemblies at the required exit access corridors. The rated assembly should be approved and/or designed by a qualified fire protection engineer in accordance with Alliance Standards. | Corrected | Mar 30 2016 | On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Sep 1 2014 | Corrected
Initial Inspection |  | 11 | There were no occupant loads posted in any buildings near the main point of egress. | Post the occupant load for every assembly and production floor in a facility in a conspicuous space near the main exit or exit access doorway for the space. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Posted. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 12 | None of the stairs have handrails on both sides in each building of the factory premises. | Install handrails on both sides of the stairs in accordance with Alliance Standards. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Installed. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Sep 1 2014 | Corrected
Initial Inspection |  | 13 | Workers are aware of the evacuation procedure upon commencing of the alarm. However, no procedure defining the evacuation process was available. | Develop an emergency evacuation plan which includes all components required by the Alliance Standards and communicate the plan to all employees as required. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Provided. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 14 | Generator shed is 7 ft far from the main building without proper fire separation. Boiler room and substation room are not fire separated from surrounding occupancy. Chemical store at ground floor shall be classified as storage (H2) according BNBC part 3 section 2.13.1.3. All these occupancy shall be separated from surrounding occupancy according to Alliance Standard 3.4.2.1. In-process goods are kept haphazardly in various floors not maintaining the requirement for miscellaneous storage (area 250 sft, height 8 ft, separation from adjacent area 10 ft) as per the Alliance Standard. | Provide fire-resistive rated construction barriers between hazard types following Table 4.4.1 of Alliance Standard. Consult a qualified fire protection engineer to design the required rated construction barrier. Keep the in-process goods on floors in a maximum area of 250 sft, height 8 ft, separation from adjacent area 10 ft. | Corrected | Jan 31 2017 | On 12/03/2017: In progress On 18-6-2017: Boiler, generator & chemical storage areas have been fire separated. Doors shall have to be kept closed otherwise shall be interfaced with FACP. In process storages are not kept as per recommendation. On 22.02.2018: Corrected as per site observation. Proper separation was found during inspection and storage was found in compliant way during inspection. On 25/09/2018: Corrected based on previous follow ups. On 24/11/2018: Corrected based on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 15 | No record of training program was available in accordance with the Alliance Safety Training Curriculum on fire safety. | Implement training program with proper documentation in accordance with the Alliance Safety Training Curriculum on fire safety. | Corrected | Jan 18 2016 | On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 16 | Fire department connections (inlet and outlet) are not provided to allow fire department pumper equipment to supplement the fire protection systems. | Fire department (Siamese) inlet connections shall be provided to allow fire department pumper equipment to supplement the fire protection systems. Fire department outlet connections shall be provided to allow fire department pumper vehicles to draw water from groundlevel or underground water storage tanks. Connections shall match the Fire Service and Civil Defence hose thread standard. | We already completed all relevant work & sent to RSC for review & waiting for verification. | Dec 31 2016 | On 24-07-16: In progress. It is an integrated part of the fire fighting system. On 12/03/2017: It is an integrated part of Fire Fighting system. On 18-6-2017: Integrated part of fire protection system. On 22.02.2018: It is an integrated part of standpipe system. On 25/09/2018: Non-listed FDC is installed. Shall be equipped with listed non-return valve. On 24/11/2018: Listed FDC shall be installed equipped with listed return valve. On 17/09/2019: It is an integrated part of standpipe system. On 29/04/2024: It is an integrated part of standpipe system On 21/01/2024: Pre T&C found that the system is not corrected. See the detailed Pre T&C report. RPO Comments: On 19-May-2026 the T&CVI documents are pending to be submitted to RSC. | Nov 24 2014 | In Progress
Initial Inspection |  | 17 | No plan or record of conducting periodic tests of the emergency battery backup for illumination of exit signs was available. | Develop a testing and maintenance program that ensures the emergency power for exit signs are to be tested at least once per year. Since a battery backup is used, these signss are required to be tested on a monthly basis. Functional testing of battery powered signs must be provided for a minimum of 90 min once per year. | Corrected | Jan 18 2016 | On 24-07-16: Corrected. Documentation present. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 18 | The parapet height is 31 inches on the main building. All occupiable roofs shall be provided with parapets or guards with a minimum height of 1067 mm (42 in.). | Provide parapets or guards for all occupied roofs of a minimum height of 1067 mm (42 in.) as per the Alliance Standard. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Provided. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 19 | There were no documents regarding periodical tests of emergency power for means of egress illumination. | Develop a testing and maintenance program that ensures the operation of all exit signs is verified at least once per year. If battery-operated signs are used, these signs shall be tested on a monthly basis. Functional testing of battery powered signs shall be provided for a minimum 90 min once per year. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Documentation present. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 20/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 20 | On the ground floor, the ceiling is open to the 1st floor to create an atrium. The atrium is not fire separated from the adjacent space. An automatic sprinkler system is also not installed. This violates the requirements of Alliance Standards. | Provide 1 hr fire resistive separation to separate the atrium from the adjacent spaces where smoke control is provided based on engineering analysis. Or, Provide 2 hr fire‐resistance rated construction to separate the atrium from rest of the building where egress paths do not pass through the atrium and where emergency workers are not required to access the atrium. | Corrected | Jan 18 2016 | On 18-01-16: N/A On 30-03-16: N/A On 24-07-16: N/A On 12/03/2017: N/A On 18-6-2017: N/A On 22.02.2018: N/A On 25/09/2018: Refer to issue 46. On 17/09/2019: Follow Issue no 46. On 29/04/2024: Refer to issue 46. | Nov 24 2014 | Corrected
Initial Inspection |  | 21 | Extinguishers are inspected monthly by factory's staff. But no document was found in support of i) annual maintenance of extinguishers by a servicing agent and ii) annual testing of nozzle of CO2 extinguisher. These are required as per NFPA 10. | Inspect, test and maintain fire extinguishers in accordance with requirements of NFPA 10. | Corrected | Jan 18 2016 | On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as on previous follow ups. On 29/04/2024: Corrected. | Nov 12 2014 | Corrected
Initial Inspection |  | 22 | The interior finish of the means of egress are of plaster and non-combustible paints. No document proving the class of interior finishes is available. | Get documents about classes of interior finishes from the manufacturer. Replace non-compliant finishes with finishes to be in accordance with Alliance standard 6.3.2 | Corrected | Jan 18 2016 | On 18-01-16: N/A On 30-03-16: N/A On 24-07-16: N/A On 12/03/2017: N/A On 18-6-2017: N/A On 17/09/2019: N/A On 29/04/2024: Corrected. | Nov 15 2014 | Corrected
Initial Inspection |  | 23 | Exits are of brick walls with plaster and water-based paints. No document proving the class of interior materials of exits is available. | Get documents about classes of interior materials of exits. Remove non-compliant materials and replace with materials meeting the requirements of class A or class B materials. | Corrected | Jan 18 2016 | On 18-01-16: N/A On 30-03-16: N/A On 24-07-16: N/A On 12/03/2017: N/A On 18-6-2017: N/A On 17/09/2019: N/A On 29/04/2024: Corrected. | Nov 15 2014 | Corrected
Initial Inspection |  | 24 | An automatic fire alarm and detection system is available in the factory. However, there is no monitoring company in Bangladesh. Fire service and civil defense are not capable of monitoring fire alarm and detection systems of the factories. | Arrange for direct connection of the fire alarm system to a central monitoring station or Fire Service and Civil Defense as per Alliance Standards. Until the time that monitoring can be set up, arrange a monitoring system using factory's own central detection system and personnel. A person shall be assigned to contact the fire department in the event of fire alarm activation. An annunciator shall be located in a constantly attended location (such as a fire control room) to alert this person. | We already completed all relevant work & sent to RSC for review & waiting for verification. | Oct 31 2016 | On 24/11/2018: T&C was conducted by Accord. Few deficiencies were observed. a) Conventional wiring in an addressable system for detector is not allowed besides compatibility is a question for this kind of installation. b) NAC extender used where the manufacturer of the two panels are different. Factory shall provide necessary document for its compatibility. c) Improper detector spacing observed. d) MCP, detectors missing where required. e) Wrong selection as well as mixture of detectors were observed. f) NAC extender panel was not fully supervised. g) NAC output current exceeds its capacity. h) Battery and voltage drop calculation found improper. i) Fire cable, module, Panel not properly sealed/ covered. j) Schematic diagram shall be posted in the FACP room. k) FACP room shall be separated from childcare room. l) Inadequate audibility observed in few places. m) Exhaust fan not properly interfaced. Installation of the overall system shall be as per NFPA 72 On 17/09/2019: T&C needed. On 29/04/2024: In progress observed. The factory has completed some modification work & other modification work is going as per last Pre-T&CVI.After complete the modification work, factory need to apply formal T&C to RSC 21/01/2024: Pre T&C found that the system is not corrected. See the detailed Pre T&C report. RPO Comments: On 19-May-2026 the T&CVI documents are pending to be submitted to RSC. | Jun 15 2014 | In Progress
Initial Inspection |  | 25 | Storage areas underneath the cutting tables are not clear of combustibles on 2nd floor of the main building. | Remove all combustibles stored underneath the cutting tables at the noted locations. | Corrected | Feb 29 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Removed. Factory shall keep area clear of storage at all times. On 12/03/2017: Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected. On 29/04/2024: Corrected. | Nov 15 2014 | Corrected
Initial Inspection |  | 26 | No dedicated Fire Safety Director was found in the factory, but the compliance manager works as a fire safety director. | Create a Fire Safety Director position and fill the position with an individual that has sufficient training to carry out the required duties. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Fire Safety Officer assigned. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected. On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 27 | Fire Department pre-planning has not been completed. | Complete fire department pre-planning activities with the local Fire Service and Civil Defense in accordance with Alliance Standard. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Provided. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 28 | Floor level is posted at each floor entrance in English and Bengali, but the stair designation is not mentioned. | Install signage adjacent to each stair door indicating the stair name and the floor level in accordance with the Alliance Standard. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Posted. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Jul 7 2014 | Corrected
Initial Inspection |  | 29 | There is no test and maintenance plan or record for testing and maintaining the installed class II standpipe system as per NFPA 25. | Establish an inspection, maintenance, and testing program for the standpipe and hose system. Program must comply with NFPA requirements. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected as per 2nd follow-up. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 30 | Signage for the standpipe system is not available. | Install required identification signs at the noted locations. Signage must comply with NFPA 14 requirements. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected as per 2nd follow-up. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per site observation. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Jul 21 2014 | Corrected
Initial Inspection |  | 31 | One electrician is available but the license is expired. Some acids are used in operations but an acid license was not found. | Re-validate the electrician license from Bangladesh Bidyut License Prodankari Board and obtain the acid license from the DC office. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Documentation present. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Jun 30 2014 | Corrected
Initial Inspection |  | 32 | A written housekeeping policy is not been established or enforced. | Establish written corporate and plant policies on housekeeping to ensure scheduled cleaning for floor, wall, ceiling, supply and return air ventilation systems. Promptly reschedule skipped cleanings. Provide a documented line of authority for authorizing a cleaning delays and rescheduling. As a general rule, the maximum tolerable deposit thickness for loose fluffy lint is 13 mm (½ in.) over a maximum of 46.5 m2 (500 ft2). Limit dense deposits to 6 mm (¼ in.) and oil saturated deposits to 3.2 mm (⅛ in.). | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Documentation present. On 12/03/2017:Corrected On 22.02.2018: Corrected. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Feb 16 2015 | Corrected
Initial Inspection |  | 33 | Inspection, maintenance, and testing procedures for the fire pump are not documented and up to date. | Establish an inspection, maintenance, and testing program for the fire pump. Program must comply with NFPA requirements. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Documentation present. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected as on previous follow ups. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 34 | No up-to-date documentation of a hot-work permit was found. | Develop a NFPA 51B-compliant hot-work permit program. In general, this program should address the process of request and approval of authorities, necessary checks prior to approval, standby fire watch and fire fighting equipment, sounding of alarm procedure, duration and expiry of permit, and re-approval procedure, etc. | Corrected | Jan 18 2016 | On 18-01-16: Corrected. On 30-03-16: Corrected. On 24-07-16: Corrected. Documentation present. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 22.02.2018: Corrected as per previous follow-up inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Nov 24 2014 | Corrected
Initial Inspection |  | 35 | No occupancy certificate is available for any building on the factory premises. | Apply to RAJUK for issuance of occupancy certificate and pursue expedition of the matter. | Corrected | Jan 18 2016 | On 18-01-16: N/A On 30-03-16: N/A On 24-07-16: N/A On 12/03/2017:N/A On 18-6-2017: N/A On 22.02.2018: N/A On 17/09/2019: N/A On 29/04/2024: Corrected. | Jul 21 2014 | Corrected
Follow Up Inspection |  | 36 | New Finding: Rooms used for combustible storage are not separated by fire-rated construction. Location: Second floor, Third Floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Sep 15 2016 | On 12/03/2017: In progress On 18-6-2017: 4th floor fabric store, 3rd floor accessories store, 2nd floor finished goods store fire separation is not completed yet. In process storages were not found defined as per recommendation. On 22.02.2018: Not completed yet. Door closure was not working properly. On 25/09/2018: Corrected. Door closure is found working properly. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 37 | New Finding: Manual on-off switch is provided for emergency lighting units. This was reflected throughout the building in various locations. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | Mar 30 2016 | On 30-03-16: Corrected. On 24-07-16: Corrected. Removed. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 29/04/2024: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 38 | New Finding in 3rd follow-up: Penetrations through floor/ceiling assemblies and exit stairs are found unsealed. | Seal all penetrations and openings in the wall of exit enclosure walls (full thickness of the wall) by fire rated materials to maintain the fire resistance rating. | Corrected | Apr 30 2016 | On 30-03-16: New Finding On 24-07-16: Corrected. Sealed. On 12/03/2017:Corrected On 18-6-2017: Corrected as per previous follow-up. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Within 1 months | Corrected
Follow Up Inspection |  | 39 | New Finding in 3rd follow-up: Areas used for in-process storage of combustible materials are open to the surrounding occupancy. Location : All the floors. | Provide defined storage areas and limit the storage arrangement as follows: 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Complete | Oct 15 2016 | On 30-03-16: New Finding On 24-07-16: In progress. Factory is not maintaining in process goods as per Accord's dimensional recommendation. On 12/03/2017: Corrected On 18-6-2017: See issue 14. On 22.02.2018: Corrected as per site observation. Storage was not found in compliant way during inspection. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Partially corrected. Found improper. On 17/09/2019: Corrected . On 29/04/2024: Reponed.In process storage area are not maintained as per standard at 3rd & 4th floor. RPO Comments: On 15-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 1 months | Pending Verification
Follow Up Inspection |  | 40 | New Finding in 5th: Exit access travel distance and dead end aisles exceed limit at 2nd floor finished goods storage area. | Exceed access travel distance shall be not more than 30 m for storage space with one exit door as per Table 4.3.3, BNBC 2006. Also provide secondary exit to meet dead end aisle requirement (Not more than 50 ft.) as per table 6.13.3, Accord building standard. | Corrected | Aug 16 2017 | NEW FINDING (5th) On 22.02.2018: Corrected as per site observation. Secondary exit has been provided. On 25/09/2018: Corrected as on previous follow ups. On 24/11/2018: Corrected On 17/09/2019: Corrected. On 29/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 41 | New Finding (6th Follow-Up): Manual on-off switch is provided for emergency lighting units. This was reflected throughout the building in various locations. | Remove manual on/off switches from emergency lighting units to prevent them from being switched off. | Corrected | May 3 2018 | On 22.02.2018: NEW FINDING. On 25/09/2018: Corrected. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 29/04/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 42 | New Finding (6th Follow-Up): Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Mar 22 2018 | On 22.02.2018: NEW FINDING. On 25/09/2018: Corrected. On 24/11/2018: Corrected. On 17/09/2019: Corrected . On 29/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 43 | New Finding (6th Follow-Up): Unsealed penetrations and openings are located in exit stair enclosures. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Corrected | Mar 22 2018 | On 22.02.2018: NEW FINDING. On 25/09/2018: Hose box (thickness is 12 inch) installed in 5 inch brick wall. In this condition total width/thickness of wall shall be 20 inch. Factory informed that they will complete it shortly which need to physical verification. On 24/11/2018: Corrected as per site observation. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 44 | New Finding (6th Follow-Up): Emergency lights not illuminated during testing (burned out, broken, etc.). | Regularly inspect all emergency lighting system as per Accord standard and replace/install lights as needed to illuminate signs. | Corrected | May 3 2018 | On 22.02.2018: NEW FINDING. On 25/09/2018: Corrected. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 45 | New Finding (6th Follow-Up): Penetrations through floor/ceiling assemblies are found unsealed. Location: Worker's Dinning. | Seal all penetrations and openings in floor/ceiling (full thickness of the floor/ceiling) assemblies by fire rated materials to maintain the fire resistance rating. Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Corrected | May 3 2018 | On 22.02.2018: NEW FINDING. On 25/09/2018: Corrected. On 24/11/2018: Corrected. On 17/09/2019: Corrected as per previous follow up. On 29/04/2024: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 46 | New Finding: Ground floor is not separated from 1st floor due to ground floor ceiling is open to 1st floor at washing and ETP section (creating atriums) . | Separate the 1st floor from the ground floor ceiling opening areas by following provisions: 1) Provide 2 hr fire‐resistance rated construction to separate the atrium from rest of the building where egress paths do not pass through the atrium and where emergency workers are not required to access the atrium (as per Accord 3.7.6.1). Or 2) Provide separation and sprinkler protection in accordance with Accord 3.7.4 and NFPA 13. Or 3) Provide 1 hr fire resistive separation to separate the atrium from the adjacent spaces where smoke control is provided based on engineering analysis as per Accord 3.7.6 and NFPA 92. | Complete | Nov 25 2018 | On 24/11/2018: No action has been taken yet. Found same as it was. On 17/09/2019: Corrected On 29/04/2024: Reopened. First floor is not separated from ground floor near load/unloading area . RPO Comments: On 15-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 2 months | Pending Verification
Follow Up Inspection |  | 47 | New Finding(10th FUI): Penetrations through fire rated floor/ceiling assemblies are not properly sealed all floor of levels. Location: Electrical BBT riser. | Seal all penetrations and openings in floor/ceiling assemblies to maintain the fire separation at least by 3-hr. The used sealer shall be 3rd party certified and installation shall be as per manufacturer's datasheet. or, Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor if required. | Complete | Jul 30 2024 | On 29/04/2024: New Finding. RPO Comments: On 15-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 48 | New Finding(10th FUI): Prayer room is not properly fire separated from other occupancy by fire rated construction. Location: 3rd floor of production building. | Separate the Prayer area from production & other occupancies by minimum 3-hr fire rated construction. Provide rated exit passageways leading directly to the exit stairs with the same resistance rating. OR Relocated the prayer room or Remove the prayer room . | Complete | Jul 30 2024 | On 29/04/2024: New Finding. RPO Comments: On 15-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification
Follow Up Inspection |  | 49 | New Finding(10th FUI): The exit discharge path not separated from the building interior due to construction of submersible pump at near exit stair-1 | Seal all penetrations and openings to the interior of the building along the discharge path, up to a height of 10 ft. to provide a minimum 2-hr fire separation. | Complete | Jul 30 2024 | On 29/04/2024: New Finding. RPO Comments: On 15-May-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | Within 3 months | Pending Verification

## Electrical
Date
19-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Unique Designers, Unique Designers Ltd, Kalemshar, K.B. Bazar,, Gazipur, Gazipur
Date of Inspection |  | 2014-05-22
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The wet type transformer is leaking, and oil level is not appropriate. | Take appropriate action to ensure that wet type transformer leak is stopped. If not able to repair, then transformer will need replacement. After repair/replacement, ensure transformer has appropriate oil levels. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 3 2014 | Corrected
Initial Inspection |  | 2 | Not all metal in the building is connected to the building's earthing/grounding system. | Connect all metal in the building to the building's earthing/grounding system. | Corrected | Sep 15 2016 | On 30/03/2016: Not corrected. Time extension given till 31/05/2016. On 18/01/2016: Not corrected. All metal in the building is not connected with earthing system. New timeline given till 29-Feb/16 . On 24/07/2016: Not Corrected. On 12/03/2017: Corrected. | Jul 1 2014 | Corrected
Initial Inspection |  | 3 | The substation room has no required fire rating/protection and is not physically separated from the remainder of the building. | Provide adequate fire rating/protection for substation room and separate the substation room from the rest of the building. | Corrected | Mar 31 2016 | On 18/01/2016: Not corrected. New timeline given till 31-March/16 to close this issue. On 30/03/2016: According to the team mate fire safety engineer, the substation room does not need additional fire separation. Hence this issue is resolved. | Jul 3 2014 | Corrected
Initial Inspection |  | 4 | No additional insulation is provided for wiring exposed to external heat sources. Location: Beside Substation East side (Frequency-2). | Provide Shielding/additional insulation for wiring exposed to external heat sources. | Corrected | Mar 31 2016 | On 30/03/2016: No such issue has been founded in this visit. Hence the issue is resolved. On 18/03/2016: Not corrected. New timeline given till 31-March/16 to close this issue. | Jun 15 2014 | Corrected
Initial Inspection |  | 5 | Multi looping of cables observed at circuit breakers within distribution boards. Location: SDB-1,Level-3 | Remove multi looping of cables at circuit breakers within distribution boards. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 3 2014 | Corrected
Initial Inspection |  | 6 | 1.Indications of overheating, overloading. 2.Signs of burning were observed. | Find out the cause of overheating, overloading, or signs of burning; take proper action to stop these occurrences; and make necessary repairs. | Corrected | Jan 31 2016 | On 30/03/2016: No such issue has been found in this visit. Thermographic scanning program has been conducted. Hence the issue is resolved. On 18/01/2016 Not corrected. Hot spot and burnt sign observed during inspection. New timeline given till 31-Jan/16 to rectify all hot points. | May 7 2014 | Corrected
Initial Inspection |  | 7 | Distribution boards are not metal enclosed with dead front construction. Location: DB-7,Level-4 | Ensure distribution boards are metal enclosed with a dead front construction. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 5 2014 | Corrected
Initial Inspection |  | 8 | Distribution boards are not installed in compliant locations (access bared/limited). | Install switchboards and/or distribution boards in compliant locations so that operation is not hampered due to limited access. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 1 2014 | Corrected
Initial Inspection |  | 9 | Wiring systems are not selected and erected considering the effect of damage caused by ingress of water. Location: Pump Room, Ground Floor. | Provide wiring systems that are selected and erected so that no damage is caused by the ingress of water. | Corrected | Feb 29 2016 | On 30/03/2016: This issue is resolved. On 18/01/2016 Not corrected. New timeline given till 29-Feb/16 to close this issue. | Jul 1 2014 | Corrected
Initial Inspection |  | 10 | Light fixtures without protective covers are installed in storage areas. Location: Chemical Room, Ground Floor | Ensure light fixtures with protective covers are installed in storage areas or in any area where the Inspector of the Factories Rules (1.5.3.5) Part 53 requires this type of fixture. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | May 7 2014 | Corrected
Initial Inspection |  | 11 | Cable trenches are not covered properly. | Provide adequate cover on cable trench. | Corrected | Mar 31 2016 | On 30/03/2016: This issue is resolved. On 18/01/2016: Not corrected. New timeline given till 31-March/16 to close this issue. | Jun 1 2014 | Corrected
Initial Inspection |  | 12 | Generator room is not properly illuminated. | Provide additional lighting for generator room to ensure that it is properly illuminated. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 15 2014 | Corrected
Initial Inspection |  | 13 | The lightning protection ground terminals are not bonded to the building or structure grounding. | Provide bonding for the lightning protection ground terminals to the building or structure grounding. | Corrected | Apr 23 2015 | On 30/03/2016: This issue is resolved. But still it is required to follow the suggestion of previous inspector. On 18/01/2016: This issue considered as corrected as the structure grounding done with present LPS, although the LPS need to modify as per reviewed drawing from Alliance. | Jul 1 2014 | Corrected
Initial Inspection |  | 14 | The substation room is not illuminated properly. | Provide additional light fixtures to increase illumination levels to appropriate levels per BNBC. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 19 2014 | Corrected
Initial Inspection |  | 15 | Electrical wiring/cables are not properly identified. Locations: SDB-1,Level-2(and in others 7 DBs) | Ensure the means of identification is obtained by separate color coding, marking tape, tagging, or other approved means. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 3 2014 | Corrected
Initial Inspection |  | 16 | Substation room is not clean and free from dirt, lint and debris. | Remove all dirt, debris, lint, water, oil, and improperly stored materials from the substation room. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | May 8 2014 | Corrected
Initial Inspection |  | 17 | Distribution boards are provided with no physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed. | Ensure switchboards and/or distribution boards provided with physical means to prevent the installation of more over current devices than that number for which the panel board was designed, rated, and listed following NFPA 70 section 408.54. | Corrected | Sep 15 2016 | On 30/03/2016: This issue has not been resolved yet. Time extension is given till 30/04/2016. On 18/01/2016: Not corrected. New timeline given till 29-Feb/16. On 24/07/2016: Not Corrected. On 12/03/2017: Not corrected. On 18/06/2017: Corrected. | Jul 3 2014 | Corrected
Initial Inspection |  | 18 | Distribution boards have no adequate capacity information labels. Locations: All DBs | Provide capacity information labels (Maximum current rating, no. of circuit breakers, etc.) for switchboards and/or distribution boards. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 19 2014 | Corrected
Initial Inspection |  | 19 | The electrical switchgear and panel boards are not inspected on an annual basis to ensure that the equipment is installed in accordance with the listed ratings. | Inspect electrical switchgear and panel boards on an annual basis to ensure that the equipment is in good working condition and provide documentation. | Corrected | Apr 30 2016 | On 30/03/2016: This issue has not been resolved yet according to the suggestion. Time extension is given till 30/04/2016.On 18/05/2016: Not corrected. New timeline given till 29-Feb/16 to close this issue. On 24/07/2016 Corrected. | Jul 3 2014 | Corrected
Initial Inspection |  | 20 | Thermographic scans of electrical equipment are not completed. | Complete thermographic scans at least on a three year cycle and maintain documentation. Thermographic scans should be completed in accordance with the Standard for Infrared Inspection of Electrical Systems & Rotating Equipment and NFPA70B or a comparable. | Corrected | May 31 2015 | On 30/03/2016: This issue had been resolved in the 1st follow-up visit. On 18/02/2016: Factory has thermographic scanning report and factory should rectify all detected hot points and maintain proper documentation. | Jul 3 2014 | Corrected
Initial Inspection |  | 21 | No evidence (test report) found to confirm that transformers do not contain any harmful substances. | Collect evidence (test report) to confirm that transformers do not contain any harmful substances. | Corrected | Sep 15 2016 | On 30/03/2016: This issue has not been resolved yet. Time extension is given till 31/05/2016. On 18/01/2016: Not corrected. New timeline given till 29-Feb/16 to close this issue. On 24/07/2016: Not Corrected. On 12/03/2017: Corrected. | Jul 3 2014 | Corrected
Initial Inspection |  | 22 | Junction boxes and other electrical devices are not provided with covers. Locations: Beside south side wall (Frequency-5) | Provide adequate covers for junction boxes and other electrical devices. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 1 2014 | Corrected
Initial Inspection |  | 23 | Generator frame earthing (grounding) is not provided at two separate points. (only 1 out of 4 generators is earthed at two points). | Provide two separate points earthing (grounding) for all generators. | Corrected | May 31 2016 | On 30/03/2016: This issue has not been resolved. Time extension is given till 31/05/2016. On 18/01/2016 Not corrected. New timeline given till 29-Feb/16 to close this issue. On 24/07/2016 Corrected. | Jun 15 2014 | Corrected
Initial Inspection |  | 24 | Electrical wiring and conduit is not properly supported. | Provide adequate supports for electrical wiring and conduit. | Corrected | Jul 15 2017 | On 30/03/2016: Still at several places the issue is remained in unsolved state. Time extension is given till 31/05/2016. On 18/01/2016: Not corrected. New timeline given till 31-March/16. On 24/07/2016:Not Corrected. On 12/03/2017: Not corrected. On 18/06/2017:Not Corrected On 22/02/2018:Not Corrected. On 25/09/2018: Not corrected. Cables around changeover & cables around few other panels are not supported. On 24/11/2018: Corrected. | Jun 15 2014 | Corrected
Initial Inspection |  | 25 | The air termination network vertical and horizontal conductors are not appropriately spaced. | Ensure the air termination network vertical and horizontal conductors are appropriately spaced. | Corrected | May 31 2015 | On 30/03/2016: LPS drawing has been amended from ALLIANCE. Time extension is given till 31/05/2016 to complete installation. On 18/01/2016: Not corrected. The LPS need to modify as per reviewed drawing from Alliance New timeline given till 29-Feb/16 to close this issue. On 24/07/2016 Corrected. | Jul 1 2014 | Corrected
Initial Inspection |  | 26 | Sockets are not provided for stranded conductors. Location: DB-3,Level-3 (Frequency-5) | Provide cable sockets for stranded conductors having a nominal cross-sectional area 6mm2 or greater. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 15 2014 | Corrected
Initial Inspection |  | 27 | Improper cable joints were found. Locations: ETP, Ground Floor(Frequency-4) | Ensure cable joints are through porcelain/PVC connectors with PIB tape wound around joints. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 15 2014 | Corrected
Initial Inspection |  | 28 | Each circuit is not provided with a dedicated neutral. Location: DB-1,Level-1 | Provide dedicated neutral for each circuit. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 3 2014 | Corrected
Initial Inspection |  | 29 | Lighting fixtures are not supported properly. Location: ETP, Ground Floor. | Ensure Lighting fixtures are supported from the structure and seismic bracing is installed as required. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 4 2014 | Corrected
Initial Inspection |  | 30 | Power and telecommunication or antenna cables are not led in separately. Location: Stair (Middle of Level-1 & Level-2). | Lay in telecommunication or antenna cables separately to the main point of service. Power and telecommunications cables must have separate entrance. | Corrected | Apr 23 2015 | This issue had been found corrected in the 1st follow-up visit. On 18/01/2016: Power and telecommunication or antenna cables are laid separately. | Jul 3 2014 | Corrected
Initial Inspection |  | 31 | Lighting and socket circuits are not separated. Location: Beside Sewing Floor, Level-4. | Lighting and socket circuits must be separated at the noted locations. Have a qualified electrician separate the lighting and sockets into separate circuits. | Corrected | Feb 29 2016 | On 30/03/2016: No such issue has been found in this visit. Hence the issue is resolved. On 18/01/2016: Not corrected. New timeline given till 29-Feb/16 to close this issue. | Jul 3 2014 | Corrected
Initial Inspection |  | 32 | Transformer oil analysis is not routinely completed on main service transformers. | Complete an oil analysis on applicable transformers at appropriate intervals based on voltage and power and provide documentation. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 3 2014 | Corrected
Initial Inspection |  | 33 | Inspection, maintenance, and testing procedures of the UPS are not completed and documented. | Ensure inspection, maintenance, and testing procedures of the UPS are completed and documented. | Corrected | May 31 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 1 2014 | Corrected
Initial Inspection |  | 34 | Inspection, maintenance, and testing procedures of the emergency generator are not being completed and documented. | Ensure inspection, maintenance, and testing procedures of the emergency generator are being completed and documented | Corrected | May 31 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 1 2014 | Corrected
Initial Inspection |  | 35 | Inadequate number of fire fighting equipment is installed inside the generator room. | Install appropriate type and number of fire fighting equipment inside the generator room. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 1 2014 | Corrected
Initial Inspection |  | 36 | No signage indicating the prohibition of light fixtures without protective covers is installed at required locations. Location: Chemical Room, Ground Floor. | Ensure signage indicating the prohibition of light fixtures without protective covers is installed at required locations. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jun 1 2014 | Corrected
Initial Inspection |  | 37 | Phase separators are not provided between terminals on circuit breakers. Location: MDB-1,Level-4 | Install phase separators between terminal connections at the noted locations. | Corrected | Apr 23 2015 | On 18/01/2016 This issue had been found corrected in the 1st follow-up visit. | Jul 1 2014 | Corrected
Follow Up Inspection |  | 38 | New Finding: No separation between LT panels and HT units (Transformer, HT switchgear ) | Make a brick built separation between LT and HT units; ensure that after making separator you have adequate ventilation (cross ventilation) and working clearance around each electrical equipment | Corrected | Dec 2 2017 | On 30/03/2016:Not corrected. Time extension is given till 31/05/2016 On 24/07/2016:Not Corrected. On 12/03/2017: Separation is not done properly though clearance around the transformer is not provided. On 18/06/2017: Corrected. | 4 Months | Corrected
Follow Up Inspection |  | 39 | New Finding: Compressor, stabilizer are not fixed at base | Fix compressor, stabilizer or any electrical equipment's at base by permanent means. | Corrected | Mar 31 2016 | On 30/03/2016: This issue is resolved. | 2 Months | Corrected
Follow Up Inspection |  | 40 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s) | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this | Corrected | Jul 15 2017 | On 30/03/2016: This issue has not been resolved throughout the factory. Time extension is given till 31/05/2016. On 24/07/2016: Not Corrected. On 12/03/2017: Not corrected. On 18/06/2017: Not Corrected. On 22/02/2018: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. | Corrected | Jul 15 2017 | On 30/03/2016: This issue has not been resolved yet. Time extension is given till 30/04/2016. On 24/07/2016: Not Corrected. On 12/03/2017: SLD is reviewed by Alliance but several suggestions need to be done. On 18/06/2017: Not Corrected. On 22/02/2018: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 42 | New Finding: Earthing system is not at satisfactory level | Factory should improve the earthing system and should do periodic testing, maintenance with proper documentation. | Corrected | May 31 2016 | On 30/03/2016: This issue has been found in incomplete state during the visit. Time extension is given till 30/04/2016 On 24/07/2016 Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 43 | New Finding: HT and Lt cable has been laid without ensuring proper separation or distance. | Provide adequate separation/distance between LT and HT cable. | Corrected | May 30 2016 | On 24/07/2016 Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Cables touching heat source. | Cables should be placed in a manner that it is not exposed to heat. Cables running along with the heat source must be separated at safe distance of 0.9m. | Corrected | Sep 15 2016 | On 12/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Cable tray is overloaded with excessive cables; eventually top cover has of no use. | Replace cable tray by wider one; or use additional cable tray to distribute cables thus 20-25% tray area are kept free (if you cover it) | Corrected | Sep 15 2016 | On 12/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust) | Clean all the cable channels/ducts; then seal them for permanent (you may use checkered/ perforated plate at the bottom). But ensure that you have used proper sized cable for all of your electrical loads. | Corrected | Jul 15 2017 | On 12/03/2017: Ducts are clean but not covered. On 18/06/2017: Not Corrected. On 22/02/2018: Not Corrected. On 25/09/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Power cables are bent excessively | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Corrected | Sep 15 2016 | On 12/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Hot spots at terminations inside panel. Thermographic inspection record is not updated. | Arrange periodic inspection & thermal scan at least twice in a year to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such point. | Corrected | Jul 15 2017 | On 12/03/2017: Not corrected. Time extension is given till 31/03/2017. On 18/06/2017: Not Corrected. On 22/02/2018: Corrected. No hot spot found during inspection. | 2 Weeks | Corrected
Follow Up Inspection |  | 49 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | Corrected | Sep 15 2016 | On 12/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Transformer Breather oil cup is empty and Silica gel is discolored. | Fill the transformer breather oil cup by transformer oil. Replace silica gel by a new one; or dry it under sun and reuse it, if color regains. | Corrected | Sep 15 2016 | On 12/03/2017: Not Corrected. On 18/06/2017: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: Higher rated circuit breakers with lower rated electrical cable. | Consult with a qualified Electrical Engineer and ensure electrical cables are sized according to capacity of circuit breakers. | Corrected | Jul 15 2017 | On 12/03/2017: Not corrected. Time extension is given till 30/04/2017. On 18/06/2017: Not Corrected. On 22/02/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Findings: Change Over Switch contacts covered with bearing grease. | Clean excess grease from the contacts. Use of grease may be avoided as it collects (sticks) dusts on the contacts. Otherwise electrically contact grease could be used. | Corrected | Sep 15 2016 | On 12/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/ undersize | Resize earth lead cable/ECC for LT panel/MDB/DB; follow BNBC 2006 Part 8 chapter 2 section 2.8 for sizing your earthing cables (Usually ECC should be equal to the half of the respective phase cable). | Corrected | Jul 15 2017 | On 12/03/2017: Not corrected. Time extension is given till 30/04/2017. On 18/06/2017: Not Corrected. On 22/02/2018: Corrected | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance) | Corrected | Sep 15 2016 | On 12/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: Electric safety training program is not initiated. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded | Corrected | Sep 15 2016 | On 12/04/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Periodicity of Transformer Oil Test (dielectric strength test) survey is not continued. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Corrected | Jul 15 2017 | On 22/02/2018: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 57 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Corrected | Jul 15 2017 | On 22/02/2018: Corrected | 2 Months | Corrected
Follow Up Inspection |  | 58 | New Finding: Factory does not have any PPE and electrical tools. | Arrange PPE and electrical tools to use during electrical installation, repair and maintenance. | Corrected | Jul 15 2017 | On 22/02/2018: Not Corrected. On 25/09/2018: Corrected. | 1Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Inadequate working space around transformer for performing maintenance work | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained | Corrected | Jun 10 2018 | On 25/09/2018: Not corrected. On 24/11/2018: Not Corrected. On 17/09/2019: Work in progress. On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 60 | New Finding: Transformer Silica gel is discolored | Silica gel shall be changed; or reuse can be done, if color regains after sundry. | Corrected | Apr 10 2018 | On 25/09/2018: Not corrected. On 24/11/2018: Not Corrected. On 17/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Oil level in transformer conservator oil tank is below minimum level. | Minimum oil level in transformer conservator oil tank must be maintained, and it shall be checked periodically. | Corrected | Apr 10 2018 | On 25/09/2018: Not corrected. There is no level indicator marking. On 24/11/2018: Not Corrected. On 17/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Power sockets are hung without proper support. | Power socket has to be installed on rigid support/base securely and at minimum 200mm above floor level. | Corrected | Apr 10 2018 | On 25/09/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Air terminals are missing, mesh width inadequate, solar panel, water tank, air condition outdoors are not protected and there is no/inadequate bond connections. LPS design is not as-built with improper roof layout drawing. | LPS need to be modified and the design shall be as-built. | Corrected | Oct 30 2018 | On 24/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Sep 30 2018 | On 24/11/2018: Not Corrected. On 17/09/2019: Not Corrected. On 09/12/2019: Corrected. | Immediately | Corrected
Follow Up Inspection |  | 65 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | Corrected | Oct 30 2018 | On 24/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Earth pit distribution information drawing is unavailable. No earth identification, no cable size information and no earth distribution information were found. | Need to prepare a detail earth distribution drawing and all earth pits shall have proper identification marking. | Corrected | Oct 30 2018 | On 24/11/2018: Not Corrected. Information are not matched with field. On 17/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: MCCBs are not adjusted per load demand. | All the MCCBs must be adjusted per connected load current; if adjustment is not possible, replacement will be the only way. | We already completed this issue | Oct 30 2018 | On 24/11/2018: Not Corrected. On 17/09/2019: Not Completed. On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: work's been started, but not finished yet. Not Corrected. On 30/11/2023: Not Corrected. Factory made progress. In few areas, adjustment mismatch found. On 25/06/2024: Not Corrected. This issue related to SLD and SLD requires to submit to RSC for review due to changes of electrical system recently. RPO Comments: On 23-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 68 | New Finding: Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. | Each electrical circuit must be terminated at single MCB/MCCB terminals. | Corrected | Oct 30 2018 | On 24/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Phase barrier/ separators are missing in MCCBs | Phases must be separated by insulator (a rubber type no-flammable materials shall be used for it) | Corrected | Oct 30 2018 | On 24/11/2018: Not Corrected. On 17/09/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Out door cables are not covered/ protected from seasonal effects. | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. | Corrected | Oct 30 2018 | On 24/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Power bus bars are installed congested; and power cables touch other phase bus bar/s | Power bus bar must be installed with adequate clearance (not less than 2.5 inch for LV) between two bars. Cables must not touch opposite bus bars in any case. | Corrected | Oct 30 2018 | On 24/11/2018: Not Corrected. On 17/09/2019: Not Completed. On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: found Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/ duct) | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Oct 30 2018 | On 24/11/2018: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Earth resistance for earth pit- 9 is too high. | Earth resistance shall be maintained within 10 ohm for lightning protection system. | Corrected | Jan 1 2020 | On 30/11/2019 Factory Asking the final timeline: 07/12/2019 Time extension is not accepted. Corrective action plan should be completed as per Accord's recommendation with immediate concern. On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: work's been started, but not finished yet. Not Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 74 | New Finding: Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | Cable ducts must be properly sealed to avoid ingression of any foreign particles. | Corrected | Nov 20 2019 | On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: work's been started, but not finished yet. Not Corrected. On 30/11/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 75 | New Finding: Electrical Distribution board/panels/tap off box are adjacent to water source. | Electrical distribution board/panels/tap off box must not be installed within 2.5meter of any water source. | Corrected | Nov 20 2019 | On 09/12/2019(Special Inspection): This issue is not under this scope of special inspection. On 16/02/2021: work's been started, but not finished yet. Not Corrected. On 30/11/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 76 | New Finding: Transformer Oil Test (dielectric strength test) report is unrealistic | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: No policies for PPE & LOTO (Lock-Out-Tag-Out) are introduced for safety of the personnel during any kind of maintenance work. Uninsulated electrical tools are used by maintenance personnel in the factory Electric safety training program document is not enriched enough. | Need to introduce and implement PPE & LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all records of using LOTO. For maintenance purposes, all the electrical tools shall be properly insulated and these insulations shall be checked periodically. It is a periodic task which factory has to continue to improve overall electrical safety situation for the staffs.(Factory may follow NFPA 70E). | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: Earth Pit resistance record is manipulated(Data copied) | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Corrected | Apr 10 2021 | On 30/11/2023: Not Corrected. ER report & field information mismatch. On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Insulation resistance test of electrical power cables is manipulated(Data copied) | Insulation resistance test of all the cables (you can avoid less than 25 sq.mm) must be performed once in every 2 years’ cycle and recorded (this must require a complete power shut off). | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Corrected | Apr 10 2021 | On 30/11/2023: Not Corrected. Significant progress has been observed. On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Distribution boards have no clear identification markings. Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present | All distribution boards, switchboards, sub main boards and switches shall be marked clearly for proper identification. CPR instruction shall be hanged near all electrical installations (LT panel, MDB, FDB, DB, SDB) at visible location | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 82 | New Finding: Field information has no/less reflection in existing SLD Electrical power cables are not identified properly | Electrical SLD must be amended properly; all the required information must be mentioned there; and it shall be updated when you do significant amount of changes of your electrical system. Proper identification (by using cable marker, tag, colored heat shrink) shall be done on major power cables used in the system according to SLD. | We already completed this issue | Apr 10 2021 | On 30/11/2023: Not Corrected. Progress has been observed. Few area cable marking pending and MCCB's and its adjustment mismatch found. On 25/06/2024: Not Corrected. Cables identification done all areas, still circuit breakers are not adjusted very few area. SLD requires to submit to RSC for review due to changes of electrical system recently. RPO Comments: On 23-Jan-2025 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 Month | Pending Verification
Follow Up Inspection |  | 83 | New Finding: Loop connection has been used powering multiple circuits through MCB/MCCBs. Multiple cables connected/terminated at the bus bar using single cable lug. | No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity) Each power cable must be terminated at any point using single cable lug. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Panel has unwanted openings. Electrical distribution box/panels are full of fluffs (lint/dirt) Tap-off box has openings | Each electrical distribution board/panel must be properly sealed to avoid ingression of fluffs; but an adequate ventilation system must also be ensured. Unwanted openings shall be sealed | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 85 | New Finding: Materials used to enclose MCCB is improper. Panel/distribution board is not firmly fixed with the foundation. | Each MCCB/MCB must be enclosed by proper type material. the material must not be more than 18 SWG graded. panel base must be securely fixed to the foundation. With appropriate fastening devices. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 86 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Corrected | Apr 10 2021 | On 30/11/2023: Not Corrected. On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 87 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 88 | New Finding: Wooden support used for electrical installation/element. Power cable is buried by concrete | Replace wooden support and it is preferable to fix each electrical devices with noncombustible support. Power cables must not be buried in the concrete. A cable trench shall be constructed or routing power cables. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 89 | New Finding: Air terminal are missing at several points of Lightning Protection System. Exposed metals are not bonded with LPS Class-2 material missing Earth electrode is undersized | Missing Air Terminals shall be reinstalled. Modification work shall be done according to acknowledged standard | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 90 | New Finding: Lead acid battery terminals are not covered properly Generator output box has openings | Lead acid battery terminals must be covered/capped and rust must be checked and cleaned. Unwanted openings shall be sealed | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 91 | New Finding: Outdoor Cable trays are not covered to protect from weather effect. Power Cables are hanging without proper support. Cable tray is overloaded with excessive cables | Outdoor cable tray/ladders shall be covered properly to avoid seasonal effect on cables and its longevity. Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. Proper sized cable tray must be installed; a perforated one is better and 20-25% space in cable tray/duct shall be kept free. | Corrected | Apr 10 2021 | On 30/11/2023: Not Corrected. Outdoor cable tray has been covered and power cable tray support provide but Cable tray overload work in progress. On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 92 | New Finding: Equipment earth cable (for generator) size is inadequate. Note: All the generators are synchronized | Equipment earth connection for generator shall be drawn from at least two separate point of generator; and the cable size shall be less than or equal to half of the phase cable (depends on fault clearing time). You may use equivalent sized bare copper conductor. Number of earth pits shall be determined by the size of connected earth cable. | Corrected | Apr 10 2021 | On 30/11/2023: Not Corrected. On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 93 | New Finding: Motor/Pumps are not earthed properly. Panel doors are not connected with earth. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 94 | New Finding: Cable termination at the motor terminal box is directly connected to terminals without proper gland. Motor cooling fan & back cover missing No mechanical guards are provided for electrical equipment where necessary. | All equipment termination must be done with proper termination including cable glands to avoid ingression of moisture and dust entering the terminals. Motor cooling fan & back cover shall be installed. Provide mechanical guards for electrical equipment where necessary. | Corrected | Apr 10 2021 | On 30/11/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 95 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Corrected | Jan 10 2024 | On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 96 | New Finding: Inadequate working space around transformer for performing maintenance work. | Minimum working space (1.07m) around the transformer (and related electrical installations) must be maintained. | Corrected | Feb 10 2024 | On 25/06/2024: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 97 | New Finding: Panel body is not connected to earth. Earthing bar installed on insulator. | All metal installation which are part of electrical system must be connected to earth to avoid electrical shock or electrocution. | Corrected | Jan 10 2024 | On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 98 | New Finding: Circuit breaker has no capacity information. | Each Circuit breaker must have its own capacity information. | Corrected | Jan 10 2024 | On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 99 | New Finding: Combustible material and water pot attached with cable duct/channels. | Cable channels/ducts must be kept neat and clean; these must be free from combustible material and water pot. | Corrected | Jan 10 2024 | On 25/06/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 100 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Corrected | Jan 10 2024 | On 25/06/2024: Corrected. | 1 Month | Corrected

## Boiler
Date
19-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | Unique Designers, Unique Designers Ltd, Kalemshar, K.B. Bazar,, Gazipur, Gazipur
Date of Inspection |  | 2022-09-29
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 7738 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 2 | BB 3932 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 3 | BB 9074 | No emergency stop push switch was available near the entrance outside of the boiler room and on the boiler control panel. | Emergency stop push switches must be installed on the boiler control panel and outside the boiler room near every entrance door. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 4 | BB 7738 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We already completed the issue. (Picture Attached As Per Item Number) | Feb 4 2026 | Comments on 28-Dec-2025: Markings should be properly done with the levels properly marked and written for clear understanding. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 5 | BB 3932 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We already completed the issue. (Picture Attached As Per Item Number) | Feb 4 2026 | Comments on 28-Dec-2025: Markings should be properly done with the levels properly marked and written for clear understanding. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 6 | BB 9074 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 7 | BB 3932 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already talk to our top management to collect documents from supplier, when we will get the document then we will submit this. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments on 19-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 8 | BB 9074 | Necessary technical documents were not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 9 | BB 7738 | Necessary technical documents (manufacturing calculations, Piping & Instrumentation diagram, water treatment design & calculation, flue gas analysis report and water treatment report) are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings and calculations, Piping and Instrumentation diagram, electrical wiring diagram, commissioning documents, data sheets of mountings, accessories and feed water pump, boiler operational and maintenance log book, operation and maintenance manual, water treatment design and calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 10 | BB 7738 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already completed the issue. | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 11 | BB 3932 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already completed the issue. | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 12 | BB 9074 | Boiler steam header and steam pipeline were found with improper insulation. | Proper insulation to exposed parts of the boiler body and steam distribution pipelines should be provided. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 13 | BB 7738 | Water leakage was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 14 | BB 3932 | Water leakage was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 15 | BB 9074 | Water leakage was observed inside the boiler room. | Boiler and its surrounding shall be free from storage, obstruction and free from slipping hazard for proper monitoring by boiler operator and other relevant maintenance technicians. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 16 | BB 7738 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer’s technical documents regarding the equipment shall be provided. | We already completed the issue. (Picture Attached As Per Item Number) | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 17 | BB 3932 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer’s technical documents regarding the equipment shall be provided. | We already completed the issue. (Picture Attached As Per Item Number) | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 18 | BB 9074 | Nameplates for feed pump and safety valve were illegible. | Name plates shall permanently be fixed on the equipment and clearly readable. Manufacturer’s technical documents regarding the equipment shall be provided. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | External visual inspection | 19 | BB 7738 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We already completed the issue. | Dec 18 2025 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 20 | BB 3932 | Fuel line connection was not terminated properly. | Any fuel line openings in boiler room shall be diverted outside of the boiler room or sealed off with a bond plug/blind flange to prevent fuel leakage. | We already completed the issue. | Dec 18 2025 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 WEEKS | Pending Verification
Initial Inspection | External visual inspection | 21 | BB 7738 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder – that does not pose fall hazard – should be provided. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 22 | BB 3932 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder – that does not pose fall hazard – should be provided. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 23 | BB 9074 | A boiler with a height of 8 feet or more was observed with an inadequate platform, ladder, and handrail, making it inaccessible. | An operation, maintenance, and inspection platform with a minimum width of 2.5 feet, a railing with a minimum height of 3.5 feet, and a ladder – that does not pose fall hazard – should be provided. | We already surrender the boiler (BB-9074) to boiler authority & remove from factory. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 24 | BB 3932 | Inconsistency was observed between the nameplate data and the CIoB provided certificate copy for the boiler regarding boiler heating surface. | Information provided in the nameplate and in the CioB provided certificate shall be consistent. Any alteration shall be approved from the CioB and a copy to be preserved on site. | We already completed the issue. | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 2 MONTHS | Pending Verification
Initial Inspection | External visual inspection | 25 | BB 7738 | The Boiler room and the boilers had insufficient clearance. | The front or rear of any boiler shall not be located nearer than 36 in. (915 mm) from any wall or structure. There shall be at least 36 in. (915 mm) of clearance on each side of the boiler to enable access for maintenance and/or inspection activities. | We already talk to our top management to solve this issue. (If Possible) | Feb 4 2026 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments on 19-May-2026: The corrective action plan should be completed as per the given recommendation with immediate concern. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 26 | BB 7738 | The steam pressure gauge range was insufficient. | The boiler pressure gauge range should be at least twice the boiler’s maximum allowable working pressure mentioned in the boiler license or in accordance with any recognized international standard. | We already completed the issue. | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work will be verified during the next follow-up inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 27 | BB 7738 | Salt and scale formation was observed on the boiler in shell, end plate, tube. Nature of scale is thin and size 1 mm | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. | We already completed the issue. (Picture Attached As Per Item Number) | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work status could not be assessed, as no image was provided. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 28 | BB 7738 | An inconsistency was observed between the readings of the boiler pressure gauge and the calibrated pressure gauge | Defective pressure gauge shall be replaced with functional gauge as per Bangladesh Boiler Regulation (BBR). | We already completed the issue. (Picture Attached As Per Item Number) | Dec 18 2025 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard by 4-Jan-2026. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 29 | BB 3932 | One or more of the available safety valves were not functioning. | The non-functioning safety valve must be repaired or replaced if necessary. | We already completed the issue. (Picture Attached As Per Item Number) | Dec 18 2025 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard by 4-Jan-2026. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 2 WEEKS | Pending Verification
Initial Inspection | Functional test inspection | 30 | BB 3932 | The Steam Pressure Limiter was missing. | Steam Pressure Limiter should be installed and kept functional. | We already completed the issue. (Picture Attached As Per Item Number) | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard within the committed timeline. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification
Initial Inspection | Functional test inspection | 31 | BB 3932 | There was no interlock for the Low Low Water (LLWL) level trip of the boiler | The Low Low Water (LLW) level tripping mechanism should be functional. | We already completed the issue. (Picture Attached As Per Item Number) | Dec 11 2025 | Comments on 28-Dec-2025: The remediation work shall be done following provided guidelines and applicable standard by 4-Jan-2026. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 WEEK | Pending Verification
Initial Inspection | Functional test inspection | 32 | BB 3932 | The Air Pressure Limiter was not functional. | Air Pressure Limiter shall be kept functional. | We already completed the issue. (Picture Attached As Per Item Number) | Jan 4 2026 | Comments on 28-Dec-2025: The remediation work status could not be assessed, as no image was provided. RPO Comments: On 10-Mar-2026 the factory management reported the remediation completion. This item will be verified in the next inspection. | 1 MONTH | Pending Verification