## Structural
Date
04-May-2026 |  | STRUCTURAL & BUILDING SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | United Knit Wears (Pvt.) Ltd., Enayetnagar, Godnail, Shiddirganj, Narayanganj, Narayanganj, Dhaka
Date of Inspection |  | 2014-05-15
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 1. Reduce all floor loads to 3 kPa maximum.. | Corrected | Jun 28 2014 | On 28/06/2014: During inspection found load within 3Kpa in all floors except 3rd floor wastage room. They were advised to reduce load immediately. On 02/03/2016: During Inspection load was found more than 3 kpa in 3rd floor. In others floor the load was within 3 kpa. On 29/03/2017: Load plan has been prepared and submitted along with DEA. Revised DEA was submitted on 30th January 2017 which is under review. During Inspection load was found less than 3kPa on 3rd floor. On 18-Dec-2017: Floor loading found below 3kPa during inspection. On 17- July-2018: Found corrected from previous follow-up inspection. During inspection, Floor load was found below 2 kPa. On 19/09/2018: Corrected from previous inspection. Floor loading was found as per accepted load plan. On 31-Jan-2024: Corrected previously. Floor loading was found as per accepted load plan (typical 2 kPa). On 21-Apr-2025: Corrected previously. During the inspection, floor loading was found within the allowable limit of the accepted load plan (2 kPa). On 27-Apr-2026: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 2 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 2. Verify in-situ stress and material properties by testing 100mm dia. concrete cores of at least 4 columns. | Corrected | Aug 31 2014 | On 28/06/2014: Core test done. Report attached in DEA report On 02/03/2016: Core test done. Report attached with DEA report. On 29/03/2017: Corrected in the previous follow up inspection. On 18-Dec-2017: Cores were taken and report were available on site. Cores were verified as per report attached to DEA. Issue found corrected from previous follow up inspection. On 17-July-2018: Core was taken as a part of concrete strength evaluation and core test location was verified in previous inspection. The issue is corrected as per previous inspection. On 19/09/2018: Corrected from previous inspection. On 31-Jan-2024: Corrected previously. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 3 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 3. Commence Detailed Engineering Assessment. | Corrected | Aug 31 2014 | On 28/06/2014: DEA report submitted to Accord. After review they were asked for revision. On 02/03/2016: Factory had submitted the DEA on March 2014 to ACCOD which need to be corrected. But factory has not been submitted yet. On 29/03/2017: Factory has submitted the revised DEA on 30th January 2017 which is under review. On 18-Dec-2017: DEA was accepted from ACCORD on 23rd November 2017. Roof top plastic tank build up were not included in drawing and number of rebar was found less than the as-built with site condition for C1A column at 1F. Factory is required to revise the documents as per discrepancy report. On 17-July-2018: Factory has produced Detail Engineering Assessment report and submitted to Accord which was accepted on 23-Nov-2018. ON 19-Sep-2018: Corrected previously. DEA of the factory was accepted by ACCORD. On 31-Jan-2024: Corrected previously. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 4 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 1. Create and actively manage loading plans for all floors | Corrected | Aug 31 2014 | On 28/06/2014: Load plan produced as part of DEA report. Although they couldn't show any copy of load plan. During inspection loading found within 3Kpa except 3rd floor wastage room. However load plan will be finalized with DEA approval. On 02/03/2016: During Inspection load was found more than 3 kappa in 3rd floor. In others floor the load was within 3 kpa. No load plan was available during inspection. Load plan will be prepared along with DEA. But factory has not been submitted yet. On 29/03/2017: Load plan has been prepared and submitted along with DEA. Revised DEA was submitted on 30th January 2017 which is under review. During Inspection load was found less than 3kPa on 3rd floor. On 18-Dec-2017: Load plan has been prepared as a part of DEA. DEA was accepted on 23rd November 2017. After completing all the remedial works, factory must follow the final load plan. Till then factory is required to follow the existing load plan which is 42psf. During inspection, floor loading observed below the allowable limit. On 17-July-2018: A set of load plan has been produced as a part of DEA which was accepted by Accord. During inspection, floor load was found below allowable limit (40 psf) of floor load plan. Factory is required to maintain before retrofitting load plan until completion of retrofitting work. After completion of retrofitting work final load plan shall have to be posted and maintained accordingly. On 19/09/2018: Load plan has been produced and accepted along with DEA. Required remedial works have been completed. During inspection, after retrofitting load plan was found posted on each floor and floor loading was below the allowable limit of posted load plan. On 31-Jan-2024: Corrected previously. Load plan has been produced and accepted along with DEA. Load plan was found posted and floor loading was found as per accepted load plan (typical 2 kPa). On 21-Apr-2025: Corrected previously. Load plan was found posted on the floors and loading was found within the allowable limit of the accepted load plan (2 kPa). On 27-Apr-2026: Previously corrected. | Within 6 Weeks | Corrected
Initial Inspection |  | 5 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 2. Complete DEA. | Corrected | Aug 31 2014 | On 28/06/2014: DEA report submitted to Accord. After review they were asked for revision On 02/03/2016: Factory had submitted the DEA on March 2014 to ACCOD which need to be corrected. But factory has not been submitted yet. On 29/03/2017: Factory has submitted the revised DEA on 30th January 2017 which is under review. On 18-Dec-2017: DEA was accepted from ACCORD on 23rd November 2017. Roof top plastic tank build up were not included in drawing and number of rebar was found less than the as-built with site condition for C1A column at 1F. Factory is required to revise the documents as per discrepancy report. On 17-July-2018: This issue was covered in DEA. DEA documents of the factory were accepted by Accord where retrofitting work is required. During inspection, it was found that factory have completed remedial work except 2 column (Grid no: F-6 & A-2) and brick wall demolishing work at different floor. Factory is required to complete remaining retrofitting work immediately. On 19/09/2018: DEA documents of the factory were accepted by Accord where retrofitting work is required. Required retrofitting works have been completed and brick walls have been replaced with lightweight glass. On 31-Jan-2024: Corrected previously. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Within 6 Weeks | Corrected
Initial Inspection |  | 6 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 1. Maintain loading plans for all floors. | Corrected | Jan 31 2015 | On 28/06/2014: During inspection I found load within 3Kpa in all floors except 3rd floor wastage room. They were advised to reduce load immediately On 02/03/2016: During Inspection load was found more than 3 kpa in 3rd floor. In others floor the load was within 3 kpa. No load plan was available during inspection. Load plan will be prepared along with DEA. But factory has not been submitted yet. On 29/03/2017: Load plan has been prepared and submitted along with DEA. Revised DEA was submitted on 30th January 2017 which is under review. During Inspection load was found less than 3kPa on 3rd floor. On 18-Dec-2017: Load plan has been prepared as a part of DEA. DEA was accepted on 23rd November 2017. After completing all the remedial works, factory must follow the final load plan. Till then factory is required to follow the existing load plan which is 42psf. During inspection, floor loading observed below the allowable limit. On 17-July-2018: A set of load plan has been produced as a part of DEA which was accepted by Accord. During inspection, floor load was found below allowable limit (40 psf) of floor load plan. Factory is required to maintain before retrofitting load plan until completion of retrofitting work. After completion of retrofitting work final load plan shall have to be posted and maintained accordingly. On 19/09/2018: Load plan has been produced and accepted along with DEA. Required remedial works have been completed. During inspection, after retrofitting load plan was found posted on each floor and floor loading was below the allowable limit of posted load plan. On 31-Jan-2024: Corrected previously. Load plan was found posted and floor loading was found as per accepted load plan (typical 2 kPa). On 21-Apr-2025: Corrected previously. Load plan was found posted on the floors and loading was found within the allowable limit of the accepted load plan (2 kPa). On 27-Apr-2026: Previously corrected. | Within 6 Months | Corrected
Initial Inspection |  | 7 | Column stresses were found to be high, loading to be reduced to 3.0 kPa | 2. Implement recommendations from DEA. | Corrected | Jan 31 2015 | On 28/06/2014: They will follow DEA instruction after DEA approval. On 02/03/2016: During Inspection load was found more than 3 kpa in 3rd floor. In others floor the load was within 3 kpa. No load plan was available during inspection. Load plan will be prepared along with DEA. But factory has not been submitted yet. On 29/03/2017: Factory has submitted the revised DEA on 30th January 2017 which is under review. Remedial work shall be carried out if required after acceptance of DEA from ACCORD. On 18-Dec-2017: DEA has been accepted from ACCORD on 23rd November 2017. As per accepted DEA, factory has to carry out remedial works. During verification inspection, retrofitting works were found started. RCC over head tank was demolished and some of the partition walls were replaced by light weight structure. Rest of the works were not started at that time. Factory management is required to complete all the remedial works within given timeline. On 17-July-2018: DEA documents of the factory were accepted by Accord where retrofitting work is required. During inspection, it was found that factory have completed remedial work except 2 column (Grid no: F-6 & A-2) and demolishing work of brick wall at different floor. Factory is required to complete remaining retrofitting work immediately. On 19/09/2018: DEA documents of the factory were accepted by Accord where retrofitting work is required. Required retrofitting works have been completed and brick walls have been replaced with lightweight glass. On 31-Jan-2024: Corrected previously. Factory had completed the remediation works. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Within 6 Months | Corrected
Initial Inspection |  | 8 | Flimsy shed roofing at the ground floor. | 1. Limit access to sheds. | Corrected | Jun 28 2014 | On 28/06/2014: Tin shed were replaced with two storey RCC building On 02/03/2016: Tin sheds were replaced with two storey RCC building. On 29/03/2017: Corrected in previous follow up; found same in current. On 18-Dec-2017: This issue has been corrected from previous follow up inspection. On 17-July-2018: Found corrected from previous follow up inspection. Flimsy shed had replaced by RC slab. On 19/09/2018: Corrected in previous inspection. On 31-Jan-2024: Corrected previously. Flimsy steel shed (Boiler shed) had replaced by RC slab and wood shed had been replaced by new RC Building. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Immediately | Corrected
Initial Inspection |  | 9 | Flimsy shed roofing at the ground floor. | 2. Have factory engineer assess the structural elements of the flimsy roofs as per BNBC wind and seismic load provisions. | Corrected | Aug 31 2014 | On 28/06/2014: They have constructed two storey go down building in place of shed and using as storage area. Capacity is unknown for this building. Therefore they were advised to submit capacity calculation and analysis report along with DEA report. On 02/03/2016: They have constructed two storey RCC building in place of shed. Capacity for the building is unknown. During 1st follow-up inspection time, factory management was advised to submit the analysis report which is not submitted yet. On 29/03/2017: This issue is required to be covered in DEA report. On 18-Dec-2017: Non-engineered shed was found demolished. The replaced RCC structure will not be covered in this ACCORD ID. On 17-July -2018: Found corrected from previous follow up inspection. Factory had replaced flimsy roof shed by RC slab. On 19/09/2018: Corrected in previous inspection. On 31-Jan-2024: Corrected previously. Flimsy steel shed (Boiler shed) had replaced by RC slab and wood shed had been replaced by new RC Building. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Within 6 Weeks | Corrected
Initial Inspection |  | 10 | Flimsy shed roofing at the ground floor. | 3. Reinforce, strengthen or remove the flimsy roofing to prevent them from being a danger | Corrected | Jun 28 2014 | On 28/06/2014: Tin shed were replaced with two storey RCC building and generator shed replaced by RCC slab On 02/03/2016: Tin shed were replaced with two storey RCC building and generator shed was replaced with RCC slab On 29/03/2017: Corrected in previous follow up; found same in current. On 18-Dec-2017: Factory management has demolished the shed. This issue has been corrected from previous follow up inspection. On 17-July -2018: Found corrected from previous follow up inspection. Factory had replaced flimsy roof shed by RC slab. On 19/09/2018: Corrected in previous inspection. On 31-Jan-2024: Corrected previously. Flimsy steel shed (Boiler shed) had replaced by RC slab and wood shed had been replaced by new RC Building. On 21-Apr-2025: Corrected previously. On 27-Apr-2026: Previously corrected. | Within 6 months | Corrected
Follow Up Inspection |  | 11 | New Findings-1: Lack of building permit and design documents (Newly Constructed: 1. Utility Building) | Collect the permit drawings from the concern authority, produce the design documents as per BNBC and submit to the RSC for review. |  | Mar 27 2024 | On 31-Jan-2024: During inspection, undocumented newly constructed two storied RC building (Utility Building) was found. Building engineer is required to collect the permit drawings from the concern authority, produce the design documents as per BNBC and submit to the RSC for review. On 21-Apr-2025: The building permit from the local authority was not available. The factory is required to collect building permit approval from the local authority. The building engineer has prepared required design documents and submitted to RSC. RSC has shared review comment which needs to be addressed with a revised submission by 20-May-2025. On 27-Apr-2026: During inspection, a permit drawing from the local authority was found on site. EA of the structure was reviewed and accepted by RSC on 25 January 2026. However, during the inspection, a discrepancy was found between the as-built drawing and the as-built condition. Number of rebar found 8 instead of 10 for column C2. The building engineer is required to update the as-built drawing with EA and submit it to RSC by 18 May 2026. Progress Status: 70% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 12 | New Findings-2: Lack of building permit and design documents (Newly Constructed: 1. Utility Building) | Carry out the remedial works after getting acceptance from RSC (if required). |  | Aug 14 2024 | On 31-Jan-2024: Building engineer is required to carry out the remedial works after getting acceptance from RSC (if required). On 21-Apr-2025: This issue will be finalized with acceptance of EA. The factory is required to complete the remediation works as per the recommendation of acceptance of EA if required. On 27-Apr-2026: Any remediation work raised from EA is required to be implemented after getting re-acceptance of EA. Progress Status: 0% | (within 6 months) | In Progress
Follow Up Inspection |  | 13 | New Findings-3: Inadequate connection and lack of as built drawings (Newly constructed: 2. single storied RC Guard Room, 3. Single storied Electrical Room) | Produce the accurate as built drawings for all structures and check the connection adequacy for sheds and submit to the RSC for review. Also, carry out the remedial works after getting acceptance from RSC (if required). |  | Mar 27 2024 | On 31-Jan-2024: During inspection, inadequate connection was observed in single storied Electrical shed. Also, no as built drawings were found for single storied Guard room and Electrical shed. Building engineer is required to produce the accurate as built drawings for all structures and check the connection adequacy for sheds and submit to the RSC for review. Also, carry out the remedial works after getting acceptance from RSC (if required). On 21-Apr-2025: The building engineer has prepared as-built drawings & design report and submitted them to RSC. The RSC has shared review comment which needs to be addressed with a revised submission by 20-May-2025. The factory is required to complete the remediation works as per the recommendation of acceptance of EA if required. On 27-Apr-2026: Safety check report of Guard Room & Electrical Room was reviewed and accepted by RSC on 25 January 2026. As per the accepted documents, the factory was required to complete the retrofitting work by March 30, 2026. Till the inspection date, the factory has just started the remediation work (the old shed over the Electrical Room has been demolished). However, during inspection, a discrepancy was found between the as-built drawing and the on-site condition; all columns on the west side were found to be brick instead of RC columns. The building engineer is required to submit it to RSC by 18 May 2026. Implement remediation work as per the revised retrofitting scheme. Progress Status: 50% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 14 | New Findings-4: Falling Hazard at Roof (Utility Building) | The factory is required intsall safety barrier (railing/parapet) to avoid falling hazard. |  | Jun 2 2025 | On 21-Apr-2025: During the inspection, it was observed that the roof of the Utility Building lacked a parapet or railing, posing a fall hazard. The factory is required install safety barrier (railing/parapet) to avoid falling hazard. On 27-Apr-2026: No action has been taken. The factory is required install safety barrier (railing/parapet) to avoid falling hazard. Progress Status: 0% | (within 6 weeks) | In Progress
Follow Up Inspection |  | 15 | New finding-5: Crack on the brick wall surface (Electrical room). | Repair the crack with a suitable method. |  | Jun 10 2026 | On 27-Apr-2026: Crack on the brick wall surface (Electrical room). Repair the crack with a suitable method. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 16 | New finding-6: Nonstructural elements found unanchored/unbraced (Utility Building). | Remove the leaned rack and anchor/brace all nonstructural elements. |  | Jun 10 2026 | On 27-Apr-2026: Nonstructural elements found unanchored/unbraced (Utility Building). Remove the leaned rack and anchor/brace all nonstructural elements. | (within 6 weeks) | In Progress
Follow Up Inspection |  | 17 | New finding-7: Water ponding on the roof slab (Main factory Building). | Improve the drainage system on the roof slab. |  | Jun 10 2026 | On 27-Apr-2026: Water ponding on the roof slab (Main factory Building). Improve the drainage system on the roof slab. | (within 6 weeks) | In Progress

## Fire
Date
04-May-2026 |  | FIRE SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | United Knit Wears (Pvt.) Ltd., Enayetnagar, Godnail, Shiddirganj, Narayanganj, Narayanganj, Dhaka
Date of Inspection |  | 2014-05-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | The boiler, and generator room is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: Ground floor separate building next to exit discharge on east side of building. | Separate the boiler, and generator room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations | Corrected | Oct 28 2016 | On 02/03/2016: Generator Room: No action has been taken yet. Generator room opens in front of stair-2 discharge. Proper separation needed with fire door. Boiler Room: No action has been taken since 1st follow-up. Penetrations found at boiler room wall along the stair-2 discharge path. Factory shall open L/C for fire doors immediately. On 12/12/2016: In progress. For generator room, status is same as previous follow-up inspection. For boiler room fire door has been provided. Unprotected openings shall be sealed by fire rated construction. For double leaf door, coordinator shall be provided. If factory wants to keep fire door open, electromagnetic door holder shall be installed and interfaced with FACP. On 15-01-17: Fire door installation work is in progress. On 29/03/2017: In progress. Generator room has not been separated yet. Generator used for fire pump room is not separated from egress path. On 10/07/2017: In progress. Boiler room fire separation is done. Generators separation have not been completed yet. On 08/10/2017: Corrected as per initial inspection report. Fire rated separation has been provided. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected on previous follow-up. Note: A stair coming from store of a two story utility building were observed open with generator room. On 30-10-2019: Corrected. (Note: A stair coming from the 2 story building is open to the generator area.) On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 2 | Areas used for combustible storage are not separated by fire rated construction. Location: G, 1, floors in storage rooms and on factory floor. | Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. | Corrected | Jul 24 2016 | On 02/03/2016: No action has been taken yet. Dedicated store rooms were found without any separation on 1st, 3rd and ground floor at knitting division (stair-3) and also at finishing area. Factory shall open L/C for fire door and shall seal all the penetrations related to dedicated store room immediately. On 12/12/2016: In progress. Defined storage area shall be maintained. For storage rooms proper fire rated separation shall be provided. On 15-01-17: Fire door installation work is in progress. On 29/03/2017: Fire door installation has not been completed yet. On 10/07/2017: Civil work and fire door installation is on going. On 08/10/2017: Corrected. Very few in process storages have been found during inspection. Dedicated storage room is located outside the main production building. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Note: Factory shall separate and seal properly all penetrations in store room by fire rated construction after complete retrofitting work. On 08/01/2019: On 30-10-2019: Refer to Issue# 17. On 02/08/2022: Refer to issue no. 17. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 3 | Flammable liquid storage area is not separated by fire-rated construction (openings, non-rated doors, penetrations). Location: Generator room southeast corner of building 55 gallon drum of fuel for generator. | separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire -rated constriction. seal and/or protected all openings to maintain the required fire separations. | Corrected | Jul 26 2016 | On 02/03/2016: No action has been taken since 1st follow-up inspection. On 12/12/2016: Corrected. Separated the diesel storage. On 15-01-17: Corrected as per last follow-up inspection. On 29/03/2017: Corrected. No flammable storage has been found. On 10/07/2017: Corrected. (Removed). On 08/10/2017: Corrected. On 24/01/2018: Corrected. (Removed.) On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 4 | Unsealed penetrations and openings are located in exit stair enclosures. location: On the southeast stairwell were their installing pipe with unsealed penetrations. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation.. | Corrected | Mar 2 2016 | On 02/03/2016: Corrected. On 12/12/2016: Corrected. On 15-01-17: Corrected. Not found. On 29/03/2017: Corrected. Not found. On 10/07/2017: Corrected. (Sealed). On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected as per previous follow-up. (Please see issue no. 25). On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 5 | The exit stairs are not separated from work areas, other space on each floor by fire-rated construction. | Provide minimum 1.5-hr fire rated doors and seal all unprotected openings to separate the exit stairs from work areas and other building spaces on all floor levels. Ensure that the fire doors are self-closing and positive latching and that they are provided with fire exit (panic) hardware where serving production floors. If fire doors are required to be held open for functional reasons, provide automatic closing devices tied to the fire alarm system. | Done | Oct 28 2016 | On 02/03/2016: No action has been taken yet. Fire doors are not finalized yet. Factory shall open L/C immediately. Note: For double lift fire doors, door coordinator shall be installed properly; If the factory wants to keep the doors open at production time, magnetic door hold device must be installed interfacing with fire alarm system. On 12/12/2016: In progress. Fire door has been installed, interfacing work is pending. Doors were found open by obstruction. For office stair (stair no.3), fire rated separation is pending. On 15-01-17: It is found same as it was before. On 29/03/2017: It is found same as it was before. On 10/07/2017: Factory is working on this issue. On 08/10/2017: Separation work hasn't been completed yet. Some unsealed penetrations have been due to retrofitting work. On 24/01/2018: In progress. Due to structural retrofitting work is going on, separation work hasn't completed yet. On 26/06/2018: During follow up inspection it was observed that installed fire doors are not interfaced properly with FACP by electro-magnetic door holder device and still exit stairs are not separated by fire rated construction due to retrofitting work. On 08/01/2019: Installed fire doors are missing proper accessories, Few doors were fond open without any automatic hold-open devices. On 30-10-2019: In progress. Factory has installed fire rated doors at the exit stairs. Magnetic door holders were present. However, some door accessories were missing: door closers were missing on some doors, as a result doors did not close during alarm condition. Door coordinators were also not functioning as per requirement. Factory shall ensure all fire rated doors are maintained and functional at all times. On 02/08/2022: Corrected. Fire doors had been found functional and accessories were working properly. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 6 | Egress doors / gates with locking features are provided at building exits, exit stairs, along egress routes, exit discharge. Location: On all floors and at exit discharges. All gates/doors were open and unlocked during the inspection. | Remove locking features from all egress doors / gates. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 29 2016 | On 02/03/2016: Partially corrected. Shutter gates with locking features were found at production floors on 4th and 3rd floors as well as at main exits of ground floor. Factory shall remove the non complying gates with locking features immediately. On 12/12/2016: Status is same as previous follow-up inspection. Shutter gates with locking features were found at 2 production floors as well as at main exits of ground floor. Non-compliant locking features were also found at dinning room. Factory shall remove the non complying gates with locking features immediately. On 15-01-17: Corrected. No locking features have been observed/ found during inspection. On 29/03/2017: Corrected. No locking features have been observed/ found during inspection. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Factory has removed non-compliant locking features from egress routes exit doors/gates. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 7 | Storage was located in all the exit stairs. | Remove all storage from exit stairs and egress paths. | Corrected | Jun 24 2016 | On 02/03/2016: No action has been taken yet. IPS , compressor and other electrical panels were found at all the exit stairs. On 12/12/2016: Partially corrected. Presence of storages under exit stairs shall be removed. On 15-01-17: Corrected. During the time of inspection no storages were found. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Not found. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Immediate | Corrected
Initial Inspection |  | 8 | Collapsible gates/ sliding doors are provided at building exits, exit stairs, along egress routes, exit discharge. Location: On all floors and at exit discharges.. | Replace all gates / sliding doors along the means of egress with side-hinged, swinging egress doors. If locks are required for security reasons, utilize special door locking features complying with NFPA 101. | Corrected | Jul 29 2016 | On 02/03/2016: Partially corrected. Shutter gates with locking features were found at production floors on 4th and 3rd floors as well as at main exits of ground floor. Factory shall remove the non complying gates with locking features immediately. On 12/12/2016: Status is same as previous follow-up inspection. Shutter gates with locking features were found at 2 production floors as well as at main exits of ground floor. Non-compliant locking features were also found at dinning room. Factory shall remove the non complying gates with locking features immediately. On 15-01-17: Corrected. No collapsible gates/ sliding door/ rolling shutter doors have been observed/ found during inspection. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Factory has removed non-compliant doors/gates from egress routes. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | within 1 months | Corrected
Initial Inspection |  | 9 | The fire alarm system is antiquated, not a listed system, and does not provide alarm and notification features consistent with acceptable standards. | Replace the fire alarm system with a new, listed addressable fire alarm system in accordance with NFPA 72. | Done | Mar 17 2016 | On 29/03/2017: Wiring has been completed. But device has not been installed yet. On 10/07/2017: Installation work is going on. On 08/10/2017: Reportedly installation has been completed. T&C by ACCORD is required. On 24/01/2018: Installation work almost completed. T&C is balanced. On 26/06/2018: Modification needed before system being accepted. The fire alarm system is mostly functional with several number of deficiencies (False alarm has been frequently occurring) that reduce the reliability and allow the system to be easily damaged. Fire Alarm Supervision of circuits and protection of wiring should be provided to increase system reliability and operational functionality. Correct documentation is needed to confirm system capabilities for operation on stand-by power. Fire door and exhaust fan interfacing was found improper. Audibility needs to be evaluated and corrected in those locations where it is inadequate. All devices must be properly secured to prevent faults and reduce operational capabilities. Discrepancies were observed between As-built drawing and on-site condition, NAC was observed in SLC loop, auxiliary power supply was found non-listed, contractor has no testing tools/equipment's, device address is not clearly marked, detector coverage area shall be comply with standard. However, fire alarm system was not functional properly. All the deficiencies shall be remediated as soon as possible as per NFPA 72 prior to acceptance test again. On 08/01/2019: Observed same as last follow-up. On 30-10-2019: In progress. Factory shall complete and maintain new system as per recommendation. Once ready, factory shall notify Accord for T&C. On 02/08/2022: Factory shall submit documents for T&C within this month. On 10/06/2024: The Pre T&C VI of Fire Alarm & Detection System has been conducted on dated 10.June.2024. The system is not ready for Full T&C VI. See the details in Pre T&C VI report. On 02-Dec-24: The remediation activities according to the last Pre T&C VI is in progress. Reported that the activities will be completed within December' 2024 and send T&C documentation to the RSC for T&CVI. On 21-Apr-25: Reportedly system installation and modification work is complete. Factory has submitted As-built drawing/documents to RSC for review on 13-mar-2025 and the documents are under review. However, during inspection the system was found active. RPO Comments On 28-Apr-2026: The design documents (FADS-2nd Submission) are pending to be submitted to RSC. | Design within 4 months, install within 9 months. | In Progress
Initial Inspection |  | 10 | Activation of the fire alarm system by a manual fire alarm station provides automatic occupant notification only on the floor of alarm and not throughout the building. | Configure the fire alarm system to initiate automatic occupant notification on all floor levels to facilitate whole building evacuation upon any manual fire alarm station activation. | Done | Mar 17 2016 | On 02/03/2016: Installation work is in progress. Factory have shown the ACCORD reviewed design of fire alarm system at the time of inspection. Fire doors, HVAC system, fire pump controls should be interfaced with FACP if applicable. Factory shall finish the work within the committed timeline. On 12/12/2016: It is an integrated part of fire alarm system. On 15-01-17: It is an integrated part of fire alarm system. On 29/03/2017: It is an integrated part of fire alarm system. On 10/07/2017: It is an integrated part of fire alarm system. On 08/10/2017: Integrated part. On 24/01/2018: It is an integrated part of fire alarm system. On 26/06/2018: It is an integrated part of fire alarm system. On 08/01/2019: Integrated part of FA system. On 30-10-2019: It is an integrated part of the fire alarm system. On 02/08/2022: It is an integrated part of the fire alarm system. On 10/06/2024: The Pre T&C VI of Fire Alarm & Detection System has been conducted on dated 10.June.2024. The system is not ready for Full T&C VI. See the details in Pre T&C VI report. On 02-Dec-24: It is an integrated part of fire alarm and detection system. On 21-Apr-25: It is an integrated part of FADS system. RPO Comments On 28-Apr-2026: The design documents (FADS-2nd Submission) are pending to be submitted to RSC. | Within 1 months | In Progress
Initial Inspection |  | 11 | Inspection, testing, and maintenance for the fire alarm system it was not in accordance with NFPA 72. | Inspect, test and maintain the fire alarm system, and keep written records on-site, in accordance with NFPA 72. | Corrected | Mar 2 2016 | On 02/03/2016: Corrected. Factory is maintaining a standard testing and maintenance checklist according to NFPA 72. On 12/12/2016: Corrected as per previous follow-up inspection. On 15-01-17: Corrected as per previous follow-up inspection. On 29/03/2017: Corrected as per previous follow-up inspection. On 10/07/2017: Corrected as per previous follow-up inspection. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected on previous follow-ups. On 30-10-2019: Corrected. On 02/08/2022: Corrected. Note: Factory shall maintain the record properly and up to date. On 02-Dec-24: Corrected. On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 12 | The building is equipped with single-station smoke alarms. Smoke alarm activation sounds only a local alarm and does not provide automatic fire alarm notification of occupants. | Remove single-station smoke alarms. Provide automatic smoke detection throughout the accordance with NFPA 72. | Corrected | Mar 17 2016 | On 02/03/2016: Installation work is in progress. Factory have shown the ACCORD reviewed design of fire alarm system at the time of inspection. Fire doors, HVAC system, fire pump controls should be interfaced with FACP if applicable. Factory shall finish the work within the committed timeline. On 12/12/2016: It is an integrated part of fire alarm system. On 15-01-17: It is an integrated part of fire alarm system. On 29/03/2017: It is an integrated part of fire alarm system. On 10/07/2017: Corrected. (Removed). On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Removed. On 08/01/2019: Corrected. On 30-10-2019: Corrected as per previous follow-up. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 6 months. | Corrected
Initial Inspection |  | 13 | Inspection, testing, and maintenance records for the emergency lighting system were not available. | Inspect, test and maintain the emergency lighting system in accordance with The ACCORD standard. Keep written records on-site. | Corrected | Mar 2 2016 | On 02/03/2016: Corrected. Factory is maintaining a standard testing and maintenance checklist according to ACCORD standard. On 12/12/2016: Corrected as per previous follow-up inspection. On 15-01-17: Corrected. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. Note: Factory shall maintain the records properly and up to date. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Initial Inspection |  | 14 | Based on the number and location of emergency lights observed, adequate illumination levels are not anticipated along egress routes. Location: On factory floor. | Test the emergency lighting system on each floor and provide additional emergency fixtures to provide adequate illumination along the means of egress. Provide a minimum illumination of 10 lux at the floor level within exit stairs and exit discharge paths and minimum 2.5 lux along exit access aisles. | Corrected | Jun 25 2016 | On 02/03/2016: In progress. Number of emergency light found is inadequate. Factory should increase the number of emergency light at every floor. On 12/12/2016: Corrected. Adequate lights have been observed. On 15-01-17: Corrected. Adequate lights have been observed. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 3 months | Corrected
Follow Up Inspection |  | 15 | New Finding in 1st follow-up: Manual on-off switch is provided for emergency lighting units. | Remove manual on/off switches from emergency lighting / exit signage units to prevent them from being switched off. | Corrected | Jul 27 2016 | On 02/03/2016: Partially corrected. Manual on-off switch was found at the time of inspection for emergency exit signage. On 12/12/2016: Corrected. Removed manual on-off options. On 15-01-17: Corrected. Removed manual on-off options. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Removed. On 08/01/2019: Corrected. On 30-10-2019: Corrected. (Some units were found with manual on/off switches, those were removed and corrected during the inspection.) On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 16 | New Finding in 2nd Follow-up: Egress door at roof top does not swing in the direction of egress travel. | Modify swing direction of egress doors to the direction of egress travel. | Corrected | Aug 28 2016 | On 02/03/2016: New Finding On 12/12/2016: It was found same as before. On 15-01-17: Corrected. Door has been modified. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 17 | New Finding in 2nd Follow-up: Areas used for in-process storage of combustible materials are open to the production floor. Location: 3rd, Ground floor. | Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. or 3. Enclose the storage area from the surrounding occupancy with a minimum 1 hour construction. | Done | Jun 27 2016 | On 02/03/2016: New Finding. On 12/12/2016: In progress. Defined storage area shall be maintained. For storage rooms proper fire rated separation shall be provided. On 15-01-17: Corrected. During the time of inspection no transient storage areas were found. On 29/03/2017: Corrected. On 10/07/2017: Corrected. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Issue reopened. Huge fire load (in-process storage) has been found on production area without maintaining any recommended arrangement. On 30-10-2019: In progress. Large amount was in-process storage was found in the production floors, but they were not maintained as per recommendation. On 02/08/2022: Observed huge in process storage at 3rd and GF. On 02-Dec-24: Corrected. The combustible in process goods have been found within limit on all the floors. On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 18 | New Finding in 2nd Follow-up: Storage located in the dining area. Location : Roof floor. | Remove storage from the dining area. | Corrected | Apr 24 2016 | On 02/03/2016: New Finding. On 12/12/2016: Corrected. Removed. On 15-01-17: Corrected. Removed. On 29/03/2017: Corrected. On 10/07/2017: Not corrected. Storage was observed during inspection. On 08/10/2017: Corrected (Removed). On 24/01/2018: Corrected. On 26/06/2018: Corrected. Removed. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Immediate | Corrected
Follow Up Inspection |  | 19 | New Finding in 2nd Follow-up: Flammable liquid storage area is not separated by fire-rated construction. Location: Void area of the building. | Separate the hazardous materials / flammable liquid storage room by a minimum 2-hr fire-rated construction. Seal and/or protected all openings to maintain the required fire separations. | Corrected | May 23 2016 | On 02/03/2016: New Finding. On 12/12/2016: Corrected. Removed. On 15-01-17: Corrected. Removed. On 29/03/2017: Corrected. On 10/07/2017: Corrected. Removed. On 08/10/2017: Corrected. On 24/01/2018: Corrected. (Removed.) On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 20 | New finding (3rd follow-up): The existing factory building with an occupiable floor greater than 10m (33 ft.) above the finished grade is not protected with an approved standpipe system. Note: Reviewed design was found during follow-up inspection & installation is in progress | Submit the as-built design of fire fighting system to Accord in accordance with NFPA 14 & installation should be as per the reviewed design | Done | Jan 12 2017 | On 15-01-17: No action has been taken yet. On 29/03/2017: L/C has not been opened for fire alarm system. On 10/07/2017: Work in progress. On 08/10/2017: Installation is still ongoing. On 24/01/2018: Installation work almost completed. T&C is balanced. On 26/06/2018: Not corrected. During follow up (testing & commissioning) inspection following observations were found: 1. Factory has installed centrifugal horizontal split case pump (both Diesel & Electric) in negative suction. 2. PRV pipe & fittings were not as per standard. 3. The pressure sensing lines for each pump are not constructed as per standard materials. 4. Suction line to the electric pump, does not meet NFPA 20 requirements, An elbow was present in the line within 10 times suction pipe diameter of the pump suction flange. 5. Diesel tank connection line does not constructed as per standard materials. 6. Fire pump pressure setting and dedicated water reservoir capacity was not as per standard. Factory shall install fire pump as per NFPA 20. Protection system (standpipe) shall be deigned as per NFPA 14 & 20 and Accord standard. On 08/01/2019: Observed same as last follow-up. On 30-10-2019: In progress. Factory shall contact the Accord for T&C when ready. On 02/08/2022: Factory shall submit documents for T&C within this month. On 10/06/2024: The Pre T&C VI of Fire Protection System has been conducted on dated 10.June.2024. The system is not ready for Full T&C VI. See the details in Pre T&C VI report. On 02-Dec-24: The remediation activities of the standpipe & fire pump system according to the last Pre T&C VI is in progress. Reported that the activities will be completed within December' 2024 and send T&C documentation to the RSC for T&CVI. On 21-Apr-25: System installation and modification work as per last pre-T&CVI report (conducted on 10-Jun-2024) is underway. Reportedly, factory will submit the updated as-built documents to RSC by 6-weeks. However, during inspection system and fire pump controllers were found active. RPO Comments On 28-Apr-2026: The design documents (as-built documents-SUPS) are pending to be submitted to RSC. | Within 1 month | In Progress
Follow Up Inspection |  | 21 | New finding (3rd follow-up): Exits are not remotely located from each other at 1st floor. | Modify exit arrangement or Provide additional exit(s) or Provide automatic sprinkler system throughout the building as per NFPA 13 | Corrected | Jan 12 2017 | New Finding (3rd follow-up inspection) On 15-01-17: It is found same as it was before. On 29/03/2017: Civil work is going on. On 10/07/2017: Civil work is on going. On 08/10/2017: Work hasn't been finished yet. On 24/01/2018: In progress. On 26/06/2018: Fire door was laid on factory yard. Factory management informed that they will complete this work after completing retrofitting work within a week. On 08/01/2019: Corrected. Exit has been modified. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 22 | New finding (3rd follow-up): Floor no., occupant load, stair designation sign were not present in the exit stairs | Provide floor no., maximum & present occupant load, stair designation sign in every stair in all floors | Corrected | Jan 12 2017 | New Finding (3rd follow-up inspection) On 15-01-17: Corrected. On 29/03/2017: Corrected. On 10/07/2017: Partially corrected. Stair designation sign was missing. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Provided. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 23 | New Finding: Unsealed penetrations and openings are located in the fire rated floor/ceiling assemblies. | Provide a minimum 2-hr fire rated shaft to separate the utility risers from each floor level. Seal all penetrations and openings in floors/ceiling assemblies to maintain the fire separation. | Corrected | Feb 15 2017 | New Finding On 29/03/2017: No action has been taken yet. On 10/07/2017: Corrected. (Sealed). On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Sealed. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 24 | New finding (6th follow-up): The width of egress aisles is less than 36-inch. On fifth floor. | Provide minimum aisle widths of 36-inch. | Corrected | Aug 10 2017 | On 10/07/2017: New Finding. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. Provided. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 25 | New finding (6th follow-up): Inspection, testing and maintenance of portable fire extinguishers is not in accordance with NFPA 10. | Inspect, test and maintain the portable fire extinguishers and keep written records onsite, in accordance with NFPA 10 and ACCORD standards. | Corrected | Aug 10 2017 | On 10/07/2017: New Finding. On 08/10/2017: Corrected. On 24/01/2018: Corrected. On 26/06/2018: Corrected. On 08/01/2019: Corrected. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 26 | New Finding (On 26/06/2018): Unsealed penetrations and openings are located in west-south exit stair enclosure throughout the building. | Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation. Seal all penetrations and openings in exit stair enclosure walls to maintain the fire separation as per Accord standard 6.3.1.3. | Corrected | Jul 26 2018 | On 26/06/2018: New Finding On 08/01/2019: Corrected. Listed Gypsum board has been found installed. On 30-10-2019: Corrected. On 02/08/2022: Corrected. On 02-Dec-24: Corrected On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 27 | New finding (12th follow-up): Dinning and prayer room are not separated by 2-hr fire rated separation from Sample section. | Separate the dining area by a minimum 2-hr fire rated construction having a direct access to exit stair. Seal and/or protected all openings to maintain the required fire separations. | Done | Oct 2 2022 | On 02/08/2022: New finding. On 02-Dec-24: Gypsum separation has been provided. However, the installer personnel did not present during the inspection to provide required clarification. On 21-Apr-25: Corrected. Separated by fire rated gypsum board (Gyproc, Fire Stop gypsum board, Type-C, UL Certification no: 20130318-R27517 & UL-design no: U412) from surrounding occupancies. | Within 2 months | Corrected
Follow Up Inspection |  | 28 | New finding (12th follow-up): Combustible materials are stored underneath the cutting tables. | Remove all combustibles stored underneath the cutting tables at the noted locations. Provide dedicated storage rooms separated by minimum 1-hr fire-rated construction. Or, separate where storage rooms are not feasible, Provide defined storage areas and limit the storage arrangement as follows:- 1. General Condition: Maximum height of 2.4m and maximum area of 23m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. 2. If sprinkler protected: maximum height of 3.66m and maximum area of 93m2. Separate areas of unenclosed combustible storage by a minimum clear distance of 3m. | Done and Some work need for Pre T & C Inspection Advice. Hopefully we will be completed within 20th November 2024. | Sep 2 2022 | On 02/08/2022: New finding. On 02-Dec-24: Corrected. Removed. On 21-Apr-25: Corrected. | Within 1 month | Corrected
Follow Up Inspection |  | 29 | New finding (12th follow-up): Compressor roomis not separated from the production area. | Separate the compressor room by a minimum 2-hr fire rated construction. Seal and/or protected all openings to maintain fire separations. |  | Oct 2 2022 | On 02/08/2022: New finding. On 02-Dec-24: Fire rated separation has been provided partially with the knitting machine room by constructing fire rated wall. Full fire separation is required to be ensured with other area like 1st floor office area and west stair discharge path. On 21-Apr-25: Work in progress. Compressor room is separated from knitting machine room by fire rated wall and the upper floor's office area was observed partially separated by fire wall and gypsum board. But, openings (exit door and exhaust fan) of the compressor room is yet to be protected and the remaining unprotected openings from the office area (located at upper floor) required to be sealed or protected to maintain the required fire separation. RPO Comments on 28-Apr-2026: The factory management is required to share the remediation update regarding this item. The corrective action plan should be completed as per the given recommendation in the inspection report & technical meeting as well with immediate concern. | Within 2 months | In Progress
Follow Up Inspection |  | 30 | New finding (13th follow-up): The fire doors at the exit stair enclosures are not interfaced with the fire alarm control system | Ensure that upon fire alarm activation, any door holder automatically release the fire rated doors. In addition, wiring of any power supply interfaced with the fire alarm module(s) for controlling the shut-down of door holder in a fail-safe manner (i.e., door holder automatically release upon loss of power to the power supply) and ensure that the door holder do not re-energize upon silencing of the fire alarm system. | Some gap. Hopefully completed within June-2026 | Jan 2 2025 | On 02-Dec-24: New finding. On 21-Apr-25: Fire doors interfacing with the FACP work is on-going. FADS system installation/modification work is underway. RPO Comments on 28-Apr-2026: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. | Within 1 month | In Progress

## Electrical
Date
04-May-2026 |  | ELECTRICAL SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | United Knit Wears (Pvt.) Ltd., Enayetnagar, Godnail, Shiddirganj, Narayanganj, Narayanganj, Dhaka
Date of Inspection |  | 2014-05-31
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection |  | 1 | Service line run on walls and entering building without supports. | Service cables laid on external walls of the building must be supported to ladders throughout the length of the cable. Flexible pipes shall not be used for long point wirings. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 2 | Service line between pole mounted transformer and building is not supported and is drawn in flexible PVC conduit. | Service line between pole mounted transformer and building must be supported (catenaries wire may be used to support the cable). | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 3 Months | Corrected
Initial Inspection |  | 3 | Generator frame and body not earthed. | Generator frame/body must be directly connected to main earth terminal. Generator frame must be earthed providing two distinct earth connection of proper size earth conductor (35sqmm). | Done | Dec 15 2015 | On 02/03/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 4 | Storage in generator room. | Remove diesel, other oil barrels and combustible materials from generator room. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 5 | Compressor machine mounted on wheel. | Compressor machine mounted on wheel must be anchored or the wheels must be locked. | Done | Dec 15 2015 | On 02/03/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 6 | The area around the IPS was damp and wet. | IPS unit must be installed at safe height or safe place such as the IPS is not in risk of ingress of water. | Done | Dec 15 2015 | 08/12/2014: Corrected. | 1 Month | Corrected
Initial Inspection |  | 7 | Large exhaust fans in production floors are directly controlled by the MCB. | Large exhaust fans must be connected through control device such that it does not restart automatically when power is restored. | Done | Aug 20 2014 | 08/12/2014: Corrected. | 1 Month | Corrected
Initial Inspection |  | 8 | Relays & other control devises are not fixed firmly on the panel board, inside boiler control panel. Board, inside boiler control panel. | Wires terminating to devices inside panel must be connected firmly and wires approaching devices must be securely fastened to avoid unintentional contact with live parts. Install slotted wiring duct to latch the cable inside the duct. | Done | Aug 20 2014 | 08/12/2014: Corrected. | 1 Month | Corrected
Initial Inspection |  | 9 | Wiring and cables installed in boiler room are not protected. | Power cables installed near boiler steam lines must be protected from external heat and moisture (may keeping sufficient clearance between steam pipes and cable/installing adequate thermal-insulation on the steam pipe/ providing heat resistant pipes. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 10 | Wirings in boiler room are drawn in flexible PVC conduit. | Heat resistant conduits may be used to protect wirings inside the boiler room to prevent the damage of cables due to external heat. | Done | Aug 20 2014 | 08/12/2014: Corrected. | 1 Month | Corrected
Initial Inspection |  | 11 | Panel base plates removed to allow cable entry. | Make circular hole at the base plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 12 | Openings in the panel top and bottom cover plate. | Make circular hole at the top plate of panels and provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material. | Done | Jun 16 2016 | On 02/03/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 13 | Panels not securely fixed to the foundation. | Panel base must be securely fixed to the foundation, with appropriate fastening devices. Panel base frame may be used on foundation to mount the panel. | Done | Dec 15 2015 | On 02/03/2016: During inspection every panel board found fixed with foundation. | 1 Month | Corrected
Initial Inspection |  | 14 | Gland holes in cable base plates left open. | Provide cable gland according to the respective cable size for cable entry and exit so that the cables are not stressed on the sharp edges of the hole of panels. Provide covers (of non-combustible material) if any additional gap remains after installing cable. | Done | Apr 15 2016 | On 02/03/2016: New committed timeline is given till 15 April, 2016. On 12/12/16: Not corrected as few areas are still pending. On 15/01/2017: Not Corrected. On 29/03/2017: Not corrected. On 10/07/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 15 | Wirings in flexible PVC conduit entering panels are not firmly fixed. | Wiring in PVC flexible conduit entering panels must be firmly fixed at the panel (base / Top) using socket and check nuts. The conduit beside the panel may be supported on cable tray or riser. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 1 Month | Corrected
Initial Inspection |  | 16 | Barrier/separators between different phases are not installed. | Install separators between different phases of MCCB. Standard separators provided by the MCCB manufacturer must be used. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Corrected. | 1 Month | Corrected
Initial Inspection |  | 17 | Distribution panel and door not connected to earth. | Provide earth connection for body and doors of metallic distribution boards using green cables preferably braid so that the metallic door remains at zero potential all the time. | Done | Dec 15 2015 | On 02/03/2016: Corrected. | 1 Month | Corrected
Initial Inspection |  | 18 | Wirings in production floors are laid in wooden ducts. | Wooden ducts may be replaced with ducts made from non-combustible materials (metal sheet) and must be closed from all sides to prevent ingression of lint. | Done | Apr 30 2016 | On 02/03/2016: Not Corrected. New committed timeline is given till 30 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Not Corrected. On 10/07/2017: Corrected. | 6 Months | Corrected
Initial Inspection |  | 19 | Wire/cable joints in wiring systems are not properly done and not protected adequately. | Joints in wires and cables must be avoided. Multiple wires joint must be strictly prohibited and all extensions must be realized at terminal or bus bars designed for such purpose. | Done | Apr 15 2016 | On 02/03/2016: Not Corrected. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Not Corrected. On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 20 | New Finding: Electrical Single Line Diagram (SLD) is not amended properly. Again SLD has inadequate information which has no effectiveness. | Amend Electrical SLD properly. Mention all the modification there as present in the factory. Prepare SLD more informative thus anyone can understand it. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Not corrected. On 10/07/2017: Not Corrected. On 08/10/2017: Not Corrected. On 24/01/2018: Circuit directory cannot locate the circuit. On 26/06/2018: Not Corrected. All panel board is not shown in SLD. On 08/01/2019: Not Corrected. On 30/01/2019: Not corrected. Factory is working on the issue. Do circuit marking adequately. On 02/08/2022: Not corrected. Some progress has bee observed but SLD is not as built. SLD need to submit to RSC for review. On 04/12/2023: Not Corrected. SLD got accepted by RSC on June 2023. Factory has started implementing SLD on 3rd, 4th & 5th floor. Mismatch (Circuit breaker, Cable, Earthing layout) observed on the substation and other floors. Cable and loads are not identified yet. On 07/10/2024: Not Corrected. Progress is ongoing, but the following issues remain unresolved: individual overload protection is still missing, identification (CB, cable, and load) is absent, and earthing is inadequate. Additionally, the factory needs to prepare and maintain an updated as-built SLD. On 21/04/2025: Not corrected. Around 75% progress was found but still oversized individual protection and missing cables identification (earthing and neutral cables) have been observed. Also, load identification has not yet been done. On 26/01/2026: Corrected. They have corrected oversized breaker, individual protection and load & cables identification as per as built drawing. | 2 Months | Corrected
Follow Up Inspection |  | 21 | New Finding: Lightning Protection System(LPS) has not installed yet. | Design and Install LPS for your factory; Factory have to submit LPS design to Accord before starting installation. | Done | May 15 2016 | On 02/03/2016: LPS drawing is found but not installed yet. New committed timeline to install LPS is given till 15 May, 2016. On 12/12/16: Improper installation. Not Corrected. On 15/01/2017: Not Corrected. Improper Installation Material. On 29/03/2017: Not corrected. Air terminal Height is 23" , cross run conductor is missing and air terminal is missing in one point. Drawing is not as built. On 10/07/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 22 | New Finding: Earth Pit resistance record is unavailable. Again, Earth pits are not identifiable. | Identify each earth pit and mark it for periodic maintenance purpose. Again, all earthing systems shall be tested for resistance on any dry day not less than once in every two years and records should be preserved. | Done | Jan 18 2016 | On 02/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 23 | New Finding: Hot spots at terminations inside panel. Thermo graphic inspection record is unavailable. | Arrange periodic inspection & thermal scan at least twice in a year to identify the overloading, loose connection, unbalanced load which may cause the excessive heat-rise and take action accordingly. However, immediately correct such points. | Done | Apr 15 2016 | On 02/03/2016: Did Thermography, but has no implication in the field. This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not corrected. On 15/01/2017: Corrected. No hotspot found during inspection. | Immediate | Corrected
Follow Up Inspection |  | 24 | New Finding: Insulation resistance test of electrical cable is not performed. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | Jan 18 2016 | On 02/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 25 | New Finding: Electric safety training program is not initiated/conducted. | Electrical safety training and awareness program for the electrical personal and workers must be initiated and recorded. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: not done in a proper manner. On 15/01/2017: Not Corrected. On 29/03/2017: Not corrected. Adequate information needed. On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 26 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment. | Develop an electrical maintenance program that includes inspections and testing of the electrical systems (preventive, proactive and breakdown maintenance). | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Not corrected. On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 27 | New Finding: Motor in the boiler room, not firmly fixed on the foundation/ frame. | Motor in boiler room must be fixed firmly on the concrete floor. | Done | Nov 18 2015 | On 02/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 28 | New Finding: Boiler room has poor/ inadequate ventilation. | Ensure cross ventilation for boiler room. | Done | Dec 18 2015 | On 02/03/2016: Factory has installed exhaust fan for ventilation. | 2 Months | Corrected
Follow Up Inspection |  | 29 | New Finding: No/Inadequate rubber (insulation) mat on the working area of distribution board/panel. | Put electrical insulation (rubber mat) on the working area of each electrical installation (Transformer/LT panel/MDB/DB/SDB/ other manual operated machineries). | Done | Apr 15 2016 | On 02/03/2016: Rubber mats are not electrical graded. This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 30 | New Finding: Generator output cables (laid on floor) are not protected and supported. | If possible route all the power cable through overhead cable tray. Or ensure adequate protection for power cables arranging cable trench with checkered plate. Do not make any arrangement that obstacle personnel's movement within working clearance. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12?16: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 31 | New Finding: Oversized circuit breakers or Circuit breakers are not adjusted accordingly. | Adjust or replace all the MCCBs/MCBs according to cable ampacity (connected load). Avoid using different sized cable at the terminals. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not Corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Not Corrected. On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 32 | New Finding: Cables terminated at electrical bus bar/MCCB without cable lugs. | Terminate all the power/earth/neutral cable with proper sized cable lug. | Done | Nov 18 2015 | On 02/03/2016: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 33 | New Finding: Power cables are bent excessively. | Avoid power cable bending in electrical system; in unavoidable case bend cables without any stress but not less than 135 degree. | Done | Jan 18 2016 | On 02/03/2016: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 34 | New Finding: Rewireable fuse (cut out fuse) used for circuit protection. | Replace rewire fuses (cut-out fuse) with MCB/MCCB. | Done | Dec 18 2015 | On 02/03/2016: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 35 | New Finding: Loop connection has used powering multiple MCBs/MCCBs. | Eliminate loop cables; use single cable for each MCBs/MCCBs. You may use bus bar to avoid multiple termination. | Done | Nov 18 2015 | On 02/03/2016: No Loop connection has been found during inspection. | 1 Month | Corrected
Follow Up Inspection |  | 36 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Seal the opening by fire rated material protecting power cables thus no smoke can pass through this. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 37 | New Finding: Personal Protective Equipment (PPE) for Electrical Work is not available. Uninsulated electrical tools are used for breakdown and preventive maintenance. | Personal Protective Equipment (PPE) must be arranged by the factory management team for the safety of their employee and worker. Insulate all the electrical tools used by the electricians/technicians. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: not corrected. On 15/01/2017: Not Corrected. On 29/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 38 | New Finding: Instruction for CPR (Cardiopulmonary Resuscitation) or Electrical shock restoration is not present. | Hang this instruction near all electrical equipment (LT panel, MDB, FDB, DB, SDB) on a visible location. | Done | Apr 15 2016 | On 02/03/2016: This issue is not corrected yet. New committed timeline is given till 15 April, 2016. On 12/12/16: Not corrected. On 15/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 39 | New Finding: MCCB is installed without any enclosure at generator output. | Need to provide electrical graded enclosure. | Done | Jun 27 2016 | On 12/12/16: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 40 | New Finding: Inadequate working space around transformer. | Adequate working space (not less than 1.07m) shall be maintained around transformer. Adequate ventilation and illumination shall also be ensured. | Done | Feb 25 2017 | On 15/01/2017: Not Corrected. New Committed timeline is given till 25/02/2017. On 29/03/2017: Not corrected. Separation between LT and HT is not adequate. On 10/07/2017: Corrected. Separation between LT and HT has been provided. | 2 Months | Corrected
Follow Up Inspection |  | 41 | New Finding: Transformer breathing system is missing. | Breathing system shall be ensured functioning. (Silica gel shall be dried or replaced, and oil cup shall be refilled up to 75% of its capacity). | Done | Feb 25 2017 | On 15/01/2017: Not Corrected. New Committed timeline is given till 25/02/2017. On 29/03/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 42 | New Finding: Thermography scanning report is unavailable. | Thermography survey must be done and recorded at least twice in a year. | Done | Jan 12 2017 | On 15/01/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 43 | New Finding: Earth pits are poorly identifiable and barely scope of periodic testing. | All the earth pits shall be properly identifiable and have adequate scope of periodic measurement. | Done | Feb 25 2017 | On 15/01/2017: Not Corrected. New Committed timeline is given till 25/02/2017. On 29/03/2017: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 44 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | May 10 2017 | On 29/03/2017: Not corrected. Time extension is given till 10/05/2017 to solve the issue. On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 45 | New Finding: Earth lead cable/Earth Continuity Conductor size is inadequate/undersize. | Earth lead cable/ Earth Continuity Conductor (ECC) must be resized by half of the phase cable. Cable size shall be selected depending on the CB's response time and phase cables' size. | Done | May 10 2017 | On 29/03/2017: Not corrected. Time extension is given till 10/05/2017 to solve the issue. On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 46 | New Finding: Cables passing through wall/floor slab are not protected at the entry/exit point(s). | Cables passing through permanent wall/floor slab must be protected. Floor to floor openings shall be sealed by proper type materials (consult with fire expert). | Done | Feb 25 2017 | On 29/03/2017: Not Corrected. On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 47 | New Finding: Insulation resistance record (cable information) doesn't match with field. | Field information must be reflected in the record and significantly lower sized cables' record shall be avoided. | Done | May 10 2017 | On 10/07/2017: Not Corrected. Insulation resistance test was not perform for all cables. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 48 | New Finding: Transformer Oil Test (dielectric strength test) report is unavailable. | Transformer oil test (dielectric strength test for oil) shall be done once in a year. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 49 | New Finding: 1. Cable trench is unlearned and cables are laid on trench floor. 2. Cable channel/duct terminals are left open for ingression of lint, dust or fluffs. | 1. A cable trench shall always be kept neat and clean; a cable tray shall be installed in the trench to ensure proper support for cables and shall be covered by checkered plate. 2. Cable ducts must be properly sealed to avoid ingression of any foreign particles. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 50 | New Finding: Wiring among different floors using flexible/rigid PVC pipe- this arrangement does not have any support for cables. | A cable ladder must be used; if it is routed through outside wall, either the cable ladder must be covered or a cable duct must be used. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 51 | New Finding: 1. Power cables entering or exiting from distribution board/panel are not properly fixed. 2. Power Cables are hanging without proper support. | 1. Power cables entering or exiting from distribution board/panel must be fixed through Panel base/top plate using proper sized cable glands (metal/PVC). 2. Power cables must be supported by cable tray (ladder- where needed). Outdoor arrangement must be covered. | Done | May 10 2017 | On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 52 | New Finding: Power cables are bent excessively. | Power cables must be installed as straight as possible; in unavoidable case, not less than 135-degree bending can be allowed. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 53 | New Finding: Unterminated live wire is kept inside the electrical panel/cable tray. | All the unterminated live power cables must be removed as soon as possible. | Done | May 10 2017 | On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 54 | New Finding: Circuit is drawn from bus bar without any protective means. | Each electrical circuit must be drawn from distribution board busbar using a proper type protection arrangement (MCCB/MCB). | Done | May 10 2017 | On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 55 | New Finding: 1. Loop connection has been used powering multiple circuits through MCB/MCCBs. 2. Multiple cables (came from different electrical consumers) terminated at MCCB terminals/ Busbar. 3. Cable connected to busbar terminal without cable lug. | 1. No loop connection shall be used; each single cable shall be terminated using cable lug (flat/I) at each terminal. Combo bus bar may be used (but incoming cable size must meet the rated capacity). 2. Each electrical circuit must be terminated at single MCB/MCCB terminals. 3. Each electrical circuit must be terminated at single busbar terminals using cable lug. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 56 | New Finding: Inadequate working space around (or in front of) board/panels and access to the board/panels is obstacles. | At least 1.07 meter (or equal to the width of board/panel, whichever is higher) working clearance must be maintained in front of each electrical board/panel. | Done | May 10 2017 | On 10/07/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 57 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Done | May 10 2017 | On 10/07/2017: Not Corrected. On 08/10/2017: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 58 | New Finding: Hazardous lights in store room / storage areas are uncovered. | Hazardous lights in store room / storage areas shall be covered by proper type material; or non-hazardous lights shall be installed in these areas. | Done | Feb 28 2018 | On 26/06/2018: Not Corrected. On 08/01/2019: Not Corrected. On 30/10/2019: Not Corrected. On 02/08/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 59 | New Finding: Inadequate working clearance around the generator/s. | Working clearance around each generator should be 1.07m. If multiple generators are installed then the gap between two generators must be equal to the width of bigger generator. Do not place radiator/exhaust to access route of the room. Place the generator exhaust to the exterior of the building in a safe location any other side except south. | Done | Mar 28 2018 | On 26/06/2018: Not Corrected. On 08/01/2019: Not Corrected. On 30/10/2019: Not Corrected. On 02/08/2022: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 60 | New Finding: Cables in service are joined (splicing) between terminations. | Splicing in the power cables shall be avoided; in unavoidable cases splicing, must be made following proper guidance. | Done | Feb 28 2018 | On 26/06/2018: Not Corrected. On 08/01/2019: Not Corrected. On 30/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 61 | New Finding: Distribution panel/board is installed without proper grout or not fixed at base. | Distribution panel/board must be installed with proper grout and fix on base by permanent means. | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/10/2019: Not Corrected. On 02/08/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 62 | New Finding: Manually operated machines (may have chance to be touched by operator/user) have no earth connection. | Each manually operated machine (may have chance to be touched by user/operator) must have earth connection. Cable selection shall be made per CB response and circuit's power demand. | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 63 | New Finding: Air terminal are missing at several points of Lightning Protection System. | Missing Air Terminals shall be reinstalled. | Done | Jul 30 2018 | On 08/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 64 | New Finding: No LOTO (Lock-Out-Tag-Out) policy is introduced for safety of the personnel during any kind of maintenance work. | Need to introduce and implement LOTO policy with LOTO (Lock-Out-Tag-Out) device instead of any other means to ensure safety of the personnel during any maintenance. Need to keep all using records. | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/10/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 65 | New Finding: There is no programmed schedule for periodical inspection & testing of electrical equipment.(includes preventive and proactive). | An electrical maintenance program shall be prepared which will include inspections and testing of the electrical systems (preventive and proactive). | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/20/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 66 | New Finding: Periodicity of Transformer Oil Test (dielectric strength, moisture content and flash point) survey is not continued. | Transformer oil test (dielectric strength, moisture, and flash point test for oil) shall be done at least once in a year. If the operation of transformer is 24/7 in the facility twice in a year is a better practice. | Done | Jul 30 2018 | On 08/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 67 | New Finding: Thermography survey report is generated without conducting any physical survey (manipulated report). Latest report is a copy of previous report except the changes of date. | Thermography survey must be done and recorded at least twice in a year. Need to generate the report with real-time images and scanned images with recommendations (if any). | Done | Jul 30 2018 | On 08/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 68 | New Finding: Insulation resistance test report is generated without conducting any physical survey (manipulated report). Latest report is a copy of previous report. | Insulation resistant test of all the cables must be performed once every 2 year cycle and recorded (this must require a complete power shut off). | Done | Jul 30 2018 | On 08/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 69 | New Finding: Earthing resistance test report is generated without conducting any physical survey (manipulated report). Latest report is a copy of previous report. | All earthing systems shall be tested for resistance on any dry day not less than once in every two years. A record of every earth test made and the result shall be kept for not less than two years and shall be available to the Inspector when required. | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/10/2019: Not corrected. Ambiguity found in report. On 02/08/2022: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 70 | New Finding: Hot Spots were observed at several points. | Hot spots must be eliminated from entire electrical system and shall be always carried forward. | Done | Jul 30 2018 | On 08/01/2019: Not Corrected. On 30/10/2019: Not corrected. Report has hotspot. Do required troubleshooting and ensure regular maintenance. On 02/08/2022: Not corrected. Some progress has been observed but still hot spot observed at several points. On 04/12/2023: Not Corrected. Hot spot found at few panels on the 1st and 2nd floor. RPO Comments On 26-Dec-2023: The factory management reported the remediation completion. This item will be verified in the next inspection. On 07/10/2024: Not Corrected. Some progress observed, still hot spot found at 2 panels. On 21/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 71 | New Finding: Substation room has inadequate ventilation. | Adequate ventilation must be maintained in sub-station room. Cross/forced ventilation must be ensured. For exhaust fan, the fan diameter must not be less than 18 inch. | Done | Jul 30 2018 | On 08/01/2019: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 72 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels/ducts must be kept neat and clean; these must be sealed properly thus no scope of ingression of fluffs. | Done | Sep 5 2022 | On 04/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 73 | New Finding: Lightning Protection System (LPS) is not maintained properly. (Air terminal missing). | Periodic maintenance shall be done to maintain LPS. | Done | Oct 5 2022 | On 04/12/2023: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 74 | New Finding: Uncovered/Perforated type cable tray/PVC pipe used for wiring in storage area. | In storage area, wiring shall be done by GI pipe/solid metal duct or concealed wiring system. | Done | Sep 5 2022 | On 04/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 75 | New Finding: Generator exhaust line is kept uninsulated. | Provide fabricated removal insulation blanket systems for engine and generator exhaust components to reduce thermal radiation and convection within the engine room. | Done | Sep 5 2022 | On 04/12/2023: Not Corrected. The factory has provided insulation for one generator out of two. RPO Comments on 2-Jul-2024: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 07/10/2024: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 76 | New Finding: Lead acid battery terminals are left open. | Lead acid battery terminals must be covered/capped and rust must be cleaned. | Done | Sep 5 2022 | On 04/12/2023: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 77 | New Finding: Equipment earth cable (for generator) is inadequate. | Provide earthing connection for generator. At least two separate earth pits shall be ensured for generator; The earth cable size shall be determined according to BNBC or Adiabatic method (considering related factors). Number of earth pits shall be determined by the size of connected earth cable. | Done | Jan 10 2024 | On 07/10/2024: Not Corrected. No progress observed. On 21/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 78 | New Finding: Heat source (or exposed steam line) is adjacent to electrical installations (cable channel/duct). | Heat source (or steam line) must be kept at least 0.9 meter apart from any electrical installation. In unavoidable case, heat source shall be covered by proper and adequate insulator. | Done | Jan 10 2024 | On 07/10/2024: Not Corrected. Some progress observed, still exposed steam lines are touching electrical appliances. On 21/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 79 | New Finding: Cable duct/channels are filled with fluffs (Lint/dust). | Cable channels and ducts must be kept clean and sealed to prevent any ingress of dust and debris. | Done | Nov 16 2024 | On 21/04/2025: Not corrected. Still dust found in several cable trays. RPO Comments On 27-Jul-2025: The factory management reported the remediation completion. This item will be verified in the next inspection. On 26/01/2026: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 80 | New Finding: Safety program is initiated but has no influence in the factory all electrical personnel. | An electrical safety training and awareness program must be established and documented for all electrical personnel. The objective of this program is to cultivate a positive shift in safety attitudes and behaviors among the team. | Done | Nov 16 2024 | On 21/04/2025: Corrected. | 1 Month | Corrected
Follow Up Inspection |  | 81 | New Finding: Lightning Protection System (LPS) is not maintained properly. Issues include missing air terminals, loose or disconnected conductors, rusty equipment, unidentifiable earthing pits etc. | Regularly scheduled maintenance procedures must be conducted to ensure the continued effectiveness and reliability of the Lightning Protection System (LPS), preserving its ability to protect against lightning strikes. | Done | Jan 16 2025 | On 21/04/2025: Corrected. | 3 Months | Corrected
Follow Up Inspection |  | 82 | New Finding: Power Cables are hanging without support. | Power cables must be supported by cable tray (ladder- where needed). Outdoor cables must be covered, if required. | Done | Dec 16 2024 | On 21/04/2025: Corrected. | 2 Months | Corrected
Follow Up Inspection |  | 83 | New Finding: Unterminated live wire is kept inside the floor. | All unterminated live power cables must be expeditiously removed. | Done | Nov 16 2024 | On 21/04/2025: Corrected. Not found anywhere. | 1 Month | Corrected
Follow Up Inspection |  | 84 | New Finding: Cables joint or tapping do not have adequate insulation and mechanical strength. | Cable joints shall be made through porcelain/PVC connectors with PIB tape wound around the joint in respect of conductivity, insulation, and mechanical strength. | Done | Nov 16 2024 | On 21/04/2025: Not corrected. Still splicing found in cable trays. RPO Comments on 18-Dec-2025: The factory management is asking for a time extension which is not accepted. The corrective action plan should be completed as per the given recommendation with immediate concern. On 26/01/2026: Corrected. | 1 Month | Corrected

## Boiler
Date
04-May-2026 |  | BOILER SAFETY
From 1st June 2020 all inspections conducted by the RMG Sustainability Council. Before 1st June 2020 all inspections conducted by the Stichting Bangladesh Accord Foundation.
Remediation Summary of Actions Required
Factory Name & Address |  | United Knit Wears (Pvt.) Ltd., Enayetnagar, Godnail, Shiddirganj, Narayanganj, Narayanganj, Dhaka
Date of Inspection |  | 2022-05-26
Finance Plan Agreed |  | Yes
Inspection Visit Type | Inspection Visit Sub Type | Item No | Bolier No | Inspection Observation | Inspection Action Plan | Factory Action Plan | Final Timeline | Inspection Comments | Inspection Timeline | Progress Status
Initial Inspection | External visual inspection | 1 | BB 4537 | No emergency stop push switch was available near the entrance outside of the boiler room. | Emergency stop push switches must be installed outside the boiler room near the entrance door. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 2 | BB 4537 | Low Low Water Level (LLWL) was not marked properly on water level gauge glass system. | The Low Low Water Level (LLWL) should be marked beside the gauge glass on a separate arrangement so that the water level can be visualized and identified clearly. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 3 | BB 4537 | Boiler manufacturer's nameplate is not available on boiler. | Boiler manufacturer's nameplate shall be available on boiler with proper technical information & boiler manufacturer name in a standard language. |  | Feb 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 4 | BB 4537 | Boiler Safety Valve outlet line is not directed outside of the boiler room. | Boiler Safety Valve outlet line should be directed outside of the boiler room with proper support & drainage system. |  | Feb 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 5 | BB 4537 | Boiler steam header, exhaust pipeline, and steam pipeline were found with improper insulation. | Proper insulation to boiler steam header, exhaust pipeline, and steam pipelines shall be provided. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 6 | BB 4537 | There is no visual flame monitoring system in place. | A visual flame monitoring system is required to be installed. |  | Feb 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 1 MONTH | In Progress
Initial Inspection | External visual inspection | 7 | BB 4537 | Boiler room is not properly illuminated. | Proper illumination shall be provided in the boiler room. Illumination shall be not less than 150 lux on the floor level. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 8 | BB 4537 | Necessary technical documents are not available to verify boiler design and operation parameters. | Documentation including manufacturing drawings & calculations, Piping & Instrumentation diagram, electrical wiring diagram, commissioning documents, datasheets of mountings, accessories & feed water pump, boiler operational & maintenance logbook, operation and maintenance manual, water treatment design & calculation, flue gas analysis report and water treatment report shall be available to verify the present condition of the boiler. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress
Initial Inspection | External visual inspection | 9 | BB 4537 | The flange of exhaust/chimney pipeline is misaligned. | All pipeline flanges must be concentrically aligned with the correct flange size, appropriately sized nuts and bolts, and gaskets where necessary. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress
Initial Inspection | Internal inspection & Hydrostatic pressure test inspection | 10 | BB 4537 | Salt and medium scale formation was observed on the waterside on the shell wall and top & bottom plates. | Cleaning is required. A water treatment station is to be used. Feed and boiler water quality and conditioning should be verified and monitored. The boiler operator should operate the boiler with proper blowdown. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 1 MONTH | In Progress
Initial Inspection | Functional test inspection | 11 | BB 4537 | The Steam Pressure Limiter is missing. | Steam Pressure Limiter shall be installed and kept functional. |  | Feb 8 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 3 WEEKS | In Progress
Initial Inspection | Functional test inspection | 12 | BB 4537 | The water level gauge glass is not protected. | The water level gauge glass must be properly protected with guard rods or covered by suitable protection housing. |  | Mar 15 2024 | On 15-Dec-25: Not Corrected. The Office of the Chief Inspector of Boilers (CIoB) cancelled the renewal application for this boiler on 28-Aug-2025 because the boiler has exceeded its service life. In accordance with the Boiler Rules, 2025, the factory shall apply to the CIoB office and obtain the required approval/renewal to operate the boiler. If approval/renewal is not obtained, the boiler shall be permanently shut down and scrapped with prior approval from the CIoB office. Until approval/renewal is obtained, the boiler shall remain out of operation. | 2 MONTHS | In Progress