## Electrical
Last Inspection Date |  | 17-Mar-2026
Corrective Action Plan - Electrical
Factory Name & Address |  | Magna Manufacturing (New Site), 13 Km Daska Road, Sialkot, Punjab, Pakistan
Factory ID |  | 25797
Date of Initial Inspection |  | 17-Mar-2026
Finance Plan Confirmed
INSPECTION TYPE | REFERENCE NUMBER | CAP ITEM NUMBER | CATEGORY | SUBCATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | REMEDIATION START DATE | REMEDIATION END DATE | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
Initial inspection | CAP-0075908 | E1 | Remediation Support | Engineering Support | Some items in the Corrective Action Plan (CAP) will require remediation by a qualified engineer. Please refer to the Remediation Plan for guidance on which tasks can be completed using internal resources and which require engineering support. | Factories should begin remediation of CAP items—such as cleaning, cable organization, and basic corrections—using internal resources. For systems or design-related remediation, engagement of a qualified Electrical Design Engineer is required. | 6 weeks | 02-Jun-2026 | 14-Jul-2026 |  |  |  | In progress
Initial inspection | CAP-0075911 | E2 | Diagrams & Drawings | Sub-station room layout drg | This section refers to the electrical rooms within the facility. During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. The absence of substation room layout drawings poses significant risks to life and fire safety within the factory premises. Without these critical documents, emergency responders and maintenance personnel may face difficulties in locating and isolating electrical faults during emergencies. This delay can result in prolonged exposure to electrical hazards, increasing the risk of electrical fires and endangering lives. Furthermore, the lack of layout drawings complicates routine maintenance, potentially leading to undetected faults and increased likelihood of equipment failure. | Develop detailed substation room layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). Ensure that all critical equipment and pathways are accurately documented. Retain the drawings along with all O&M information for the facility. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075912 | E3 | Diagrams & Drawings | Sub-station room layout drg | This section refers to the electrical rooms within the facility. During the inspection conducted, it was observed that there were no substation room layout drawings available for the factory. There are no visible indications of substation equipment locations or pathways for maintenance and emergency access. The absence of substation room layout drawings poses significant risks to life and fire safety within the factory premises. Without these critical documents, emergency responders and maintenance personnel may face difficulties in locating and isolating electrical faults during emergencies. This delay can result in prolonged exposure to electrical hazards, increasing the risk of electrical fires and endangering lives. Furthermore, the lack of layout drawings complicates routine maintenance, potentially leading to undetected faults and increased likelihood of equipment failure. | Regularly update and review the substation room layout drawings to reflect any changes in equipment or configuration. Provide training sessions for maintenance personnel and emergency responders on how to interpret and utilize the layout drawings. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075909 | E4 | Diagrams & Drawings | Single Line Diagram (SLD) | This section refers to the entire facility. It was found that the electrical single line diagrams (SLDs) for the factory were missing. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. Single line diagrams are crucial for understanding the electrical distribution network and for troubleshooting issues effectively. Without these diagrams, maintenance personnel and emergency responders lack critical information necessary for isolating faults and managing power during emergencies. This can lead to delays in addressing electrical issues, increasing the risk of electrical fires and potential harm to personnel. Moreover, the lack of SLDs complicates routine maintenance and inspection processes, potentially resulting in undetected electrical faults and system inefficiencies. | Develop comprehensive electrical single line diagrams for the entire facility in accordance with the requirements outlined in Section 514.9.1 of BS7671 18th Edition + A2 (2022). Ensure all components and connections are accurately represented. Retain the drawings along with all O&M information for the facility. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075910 | E5 | Diagrams & Drawings | Single Line Diagram (SLD) | This section refers to the entire facility. It was found that the electrical single line diagrams (SLDs) for the factory were missing. This deficiency was noted in all electrical rooms and areas where SLDs should be prominently displayed. The factory lacks documented diagrams that illustrate the electrical distribution system, including the connection and configuration of all electrical components. Single line diagrams are crucial for understanding the electrical distribution network and for troubleshooting issues effectively. Without these diagrams, maintenance personnel and emergency responders lack critical information necessary for isolating faults and managing power during emergencies. This can lead to delays in addressing electrical issues, increasing the risk of electrical fires and potential harm to personnel. Moreover, the lack of SLDs complicates routine maintenance and inspection processes, potentially resulting in undetected electrical faults and system inefficiencies. | Implement a regular review and update process for the single line diagrams to reflect any changes in the electrical system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the diagrams. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075913 | E6 | Diagrams & Drawings | Electrical layout drawing | This section refers to the entire facility. During the survey, it was noted that the drawings available with the factory lacked essential electrical layout drawings, including small power layouts, lighting layouts, and containment layouts. Furthermore, the available drawings were not up to standard and did not reflect actual site conditions. This absence was consistent across all areas where such documentation should be available. These drawings are vital for understanding the placement and connections of electrical systems, which is crucial for identifying and mitigating potential hazards. In emergencies, the lack of detailed layouts can delay the identification and isolation of electrical faults, increasing the risk of fire and electrical accidents. Additionally, without proper layout drawings, routine inspections and maintenance may overlook critical issues, potentially leading to system failures and safety breaches. | Update electrical layout drawings in accordance with the requirements outlined in Sections 132.12 and 132.13 of BS7671 18th Edition + A2 (2022). To avoid drawings becoming overcrowded, separate drawings shall be prepared for each electrical system. Retain the drawings along with all O&M information for the facility. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075914 | E7 | Diagrams & Drawings | Electrical layout drawing | This section refers to the entire facility. During the survey, it was noted that the drawings available with the factory lacked essential electrical layout drawings, including small power layouts, lighting layouts, and containment layouts. Furthermore, the available drawings were not up to standard and did not reflect actual site conditions. This absence was consistent across all areas where such documentation should be available. These drawings are vital for understanding the placement and connections of electrical systems, which is crucial for identifying and mitigating potential hazards. In emergencies, the lack of detailed layouts can delay the identification and isolation of electrical faults, increasing the risk of fire and electrical accidents. Additionally, without proper layout drawings, routine inspections and maintenance may overlook critical issues, potentially leading to system failures and safety breaches. | Implement a regular review and update process for the electrical layout drawings to reflect any changes in the system. Conduct training sessions for maintenance personnel and emergency responders on interpreting and using the layouts. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076103 | E8 | DBs & Elec Protection Systems | Circuit breakers | This section refers to the entire facility. During the survey the circuit breakers installed throughout the facility inside the electrical panels and distribution boards were inspected. i. It was observed that the circuit breaker is improperly mounted without secure fixing or proper enclosure, with exposed and loosely routed cables through inadequately terminated flexible conduits and unsealed entries. This condition may lead to loose connections, overheating, arcing, short circuits, and increased risk of electric shock due to exposure of live parts and mechanical stress on terminations. The issue was noted at LT room. ii. It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. a) LT Panel: 35 sq. mm cable connected to a 200A circuit breaker. b) Storage Area DB (Ground Floor): 4 sq. mm cable connected to a 100A circuit breaker. c) Corridor DB (Ground Floor): 4 sq. mm cable connected to a 100A circuit breaker. d) Office DB (First Floor): 4 sq. mm cable connected to a 60A circuit breaker. Specifically, some circuit breakers had higher ratings than the cables could safely handle, which poses a significant risk of overheating and potential fire hazards. Conversely, other circuit breakers had lower ratings than necessary, resulting in frequent and unnecessary tripping. To ensure both safety and operational efficiency, corrective action is required to align the circuit breaker ratings with the cable capacities. This adjustment will mitigate the risks associated with overheating and improve the reliability of the electrical system. | i. Securely mount the circuit breaker in a proper enclosure with adequate IP rating, ensuring all cable entries are gland-sealed, conduits are properly terminated and supported, and no conductors remain exposed. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076104 | E9 | DBs & Elec Protection Systems | Circuit breakers | This section refers to the entire facility. During the survey the circuit breakers installed throughout the facility inside the electrical panels and distribution boards were inspected. i. It was observed that the circuit breaker is improperly mounted without secure fixing or proper enclosure, with exposed and loosely routed cables through inadequately terminated flexible conduits and unsealed entries. This condition may lead to loose connections, overheating, arcing, short circuits, and increased risk of electric shock due to exposure of live parts and mechanical stress on terminations. The issue was noted at LT room. ii. It was observed that multiple circuit breakers had ratings that were not appropriate for the connected cable sizes. a) LT Panel: 35 sq. mm cable connected to a 200A circuit breaker. b) Storage Area DB (Ground Floor): 4 sq. mm cable connected to a 100A circuit breaker. c) Corridor DB (Ground Floor): 4 sq. mm cable connected to a 100A circuit breaker. d) Office DB (First Floor): 4 sq. mm cable connected to a 60A circuit breaker. Specifically, some circuit breakers had higher ratings than the cables could safely handle, which poses a significant risk of overheating and potential fire hazards. Conversely, other circuit breakers had lower ratings than necessary, resulting in frequent and unnecessary tripping. To ensure both safety and operational efficiency, corrective action is required to align the circuit breaker ratings with the cable capacities. This adjustment will mitigate the risks associated with overheating and improve the reliability of the electrical system. | ii. Evaluate the breaker ratings and cable sizes for all circuits in the facility according to Section 433.1.1 and Appendix 4 of BS 7671 18th Edition + A2 (2022). Ensure that the breaker rating does not exceed the cable's current-carrying capacity. If the breaker has adjustable settings, they must be configured to allow current within the cable's ampacity after applying derating factors. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076107 | E10 | DBs & Elec Protection Systems | Hot Spots | This relates to the entire facility. During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards. Hot spots in electrical distribution systems can be caused by several factors, including: > Loose connections > Overloaded circuits > Faulty components > Improper sized cable > Insulation degradation It was also found that the thermographic report was not available at the site. Without thermography testing, faults such as overheating components or loose connections may go unnoticed, which increases the risk of fire. Early detection through thermography can prevent fire incidents. The categories of identified hot spots have been evaluated as per the ANSI NETA MTS 2019 standard, Table 100.18. Hot spots were observed, particularly at the following locations: i. 73°C hotspot found at the LT panel. ii. 84.8°C recorded in the first floor office area. iii. 70.8°C recorded in the cutting machine area. iv. Elevated temperature observed in the first floor area at the solar DB (hybrid inverter). Circuit breakers are typically designed to operate safely within an ambient temperature range of -20°C to 40°C. Commonly used PVC insulated cables typically have a maximum operating temperature of 70°C. Prolonged exposure to temperatures above these can degrade the insulation of the breaker as well as the cable and result in reduced performance. Hot spots in electrical systems pose significant life safety risks due to several factors. Overheated components can ignite surrounding materials, leading to electrical fires. This is particularly dangerous in densely packed panels and distribution boards where flammable materials may be present. Hot spots can degrade insulation on wires and components, increasing the risk of electrical shock to personnel who might come into contact with exposed conductive parts. Overheating can contribute to conditions that might trigger an arc flash, a dangerous high-temperature event that can cause severe injuries or fatalities to personnel working near the affected equipment. | Any circuits identified on site with temperatures exceeding 40°C above the ambient temperature, operating above 90°C or exhibiting visual signs of burning must be immediately isolated and taken out of service. These circuits should remain de-energized until a thorough review has been conducted and appropriate remedial actions have been implemented to resolve the underlying issues. | 2 days | 28-Jul-2026 | 30-Jul-2026 |  |  |  | In progress
Initial inspection | CAP-0076108 | E11 | DBs & Elec Protection Systems | Hot Spots | This relates to the entire facility. During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards. Hot spots in electrical distribution systems can be caused by several factors, including: > Loose connections > Overloaded circuits > Faulty components > Improper sized cable > Insulation degradation It was also found that the thermographic report was not available at the site. Without thermography testing, faults such as overheating components or loose connections may go unnoticed, which increases the risk of fire. Early detection through thermography can prevent fire incidents. The categories of identified hot spots have been evaluated as per the ANSI NETA MTS 2019 standard, Table 100.18. Hot spots were observed, particularly at the following locations: i. 73°C hotspot found at the LT panel. ii. 84.8°C recorded in the first floor office area. iii. 70.8°C recorded in the cutting machine area. iv. Elevated temperature observed in the first floor area at the solar DB (hybrid inverter). Circuit breakers are typically designed to operate safely within an ambient temperature range of -20°C to 40°C. Commonly used PVC insulated cables typically have a maximum operating temperature of 70°C. Prolonged exposure to temperatures above these can degrade the insulation of the breaker as well as the cable and result in reduced performance. Hot spots in electrical systems pose significant life safety risks due to several factors. Overheated components can ignite surrounding materials, leading to electrical fires. This is particularly dangerous in densely packed panels and distribution boards where flammable materials may be present. Hot spots can degrade insulation on wires and components, increasing the risk of electrical shock to personnel who might come into contact with exposed conductive parts. Overheating can contribute to conditions that might trigger an arc flash, a dangerous high-temperature event that can cause severe injuries or fatalities to personnel working near the affected equipment. | During the inspection, several circuits were identified where the temperature was exceeding 20°C above ambient temperature. It is recommended that the factory conducts comprehensive thermographic surveys of all electrical panels to detect similar issues. Identified hot spots should be thoroughly reviewed to determine their underlying causes. Corrective actions must be taken to address and resolve these issues, ensuring safe and reliable operation of the electrical systems. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076109 | E12 | DBs & Elec Protection Systems | Hot Spots | This relates to the entire facility. During the inspection, Thermographic surveys were conducted on the electrical boards. The survey identified numerous hot spots within panels and distribution boards. Hot spots in electrical distribution systems can be caused by several factors, including: > Loose connections > Overloaded circuits > Faulty components > Improper sized cable > Insulation degradation It was also found that the thermographic report was not available at the site. Without thermography testing, faults such as overheating components or loose connections may go unnoticed, which increases the risk of fire. Early detection through thermography can prevent fire incidents. The categories of identified hot spots have been evaluated as per the ANSI NETA MTS 2019 standard, Table 100.18. Hot spots were observed, particularly at the following locations: i. 73°C hotspot found at the LT panel. ii. 84.8°C recorded in the first floor office area. iii. 70.8°C recorded in the cutting machine area. iv. Elevated temperature observed in the first floor area at the solar DB (hybrid inverter). Circuit breakers are typically designed to operate safely within an ambient temperature range of -20°C to 40°C. Commonly used PVC insulated cables typically have a maximum operating temperature of 70°C. Prolonged exposure to temperatures above these can degrade the insulation of the breaker as well as the cable and result in reduced performance. Hot spots in electrical systems pose significant life safety risks due to several factors. Overheated components can ignite surrounding materials, leading to electrical fires. This is particularly dangerous in densely packed panels and distribution boards where flammable materials may be present. Hot spots can degrade insulation on wires and components, increasing the risk of electrical shock to personnel who might come into contact with exposed conductive parts. Overheating can contribute to conditions that might trigger an arc flash, a dangerous high-temperature event that can cause severe injuries or fatalities to personnel working near the affected equipment. | Regular thermographic inspections should be incorporated into the maintenance schedule to proactively manage and mitigate the risks associated with overheating. Submit the thermographic test report to the Pakistan Accord for review. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076118 | E13 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | i. Design and evaluate the earthing system installation throughout the facility by preparing a comprehensive earthing system diagram, including identification of all earthing and neutral system components. Ensure compliance with BS 7671: 18th Edition + A2 (2022), Regulation 514.5.1 regarding proper identification and labeling and, submit it to Pakistan Accord for review. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076119 | E14 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | ii. Relocate and redesign earth pits to make them easily accessible for maintenance and inspection, complying with BS 7671 18th Edition + A2 (2022) Chapter 54. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076120 | E15 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | iii. Replace all earthing cables with appropriately sized cables as per the requirements of BS 7671 18th Edition + A2 (2022) Appendix 4, Section 5. Verify that all earthing conductors meet the minimum cross-sectional area specified. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076121 | E16 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | iv. Install earthing systems where absent, ensuring compliance with BS 7671 18th Edition + A2 (2022) Chapter 54. Fit all electrical boards with the required earthing cables. Ensure that earthing conductors are properly connected and comply with BS 7671 18th Edition + A2 (2022) Section 543.1. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076122 | E17 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | v. Provide equipotential bonding for all cable trays, metallic panel covers, and other exposed conductive parts, complying with BS 7671: 18th Edition + A2 (2022). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076123 | E18 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | vi. Prepare and submit the earth testing record to the Pakistan Accord for review. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076124 | E19 | DBs & Elec Protection Systems | Earthing system | This relates to the entire facility. During the inspection of the facility's electrical panels, distribution boards, and machinery, several observations with the earthing system were identified. i. Comprehensive drawings for the earthing system were absent. The lack of proper documentation and identification of the earthing and neutral system components pose safety risks. ii. The earth pits were inaccessible and unsuitably located outside the factory. iii. The earthing cables were not appropriately sized according to the relevant earthing standards at LT panel, LT room. iv. The earthing system was absent in multiple locations. Several distribution boards lacked earthing cables, and many electrical machines did not have proper earth connections. The issue was noted at storage area, water cooler, stitching machines, cable tray and metal fixings. v. Equipotential bonding for the cable trays and metallic panel covers was missing at distribution boards and cable tray installed on first floor. vi. It was found that the earth testing record was not available at the site. Without earth testing records, it is difficult to ensure that the grounding system is functioning correctly and that maintenance activities are being properly conducted. The lack of proper earthing system throughout the facility poses substantial safety risks, such as electric shocks, fires, and equipment damage. Implementing appropriate earthing measures is crucial to prevent hazardous voltage levels and ensure operational safety. | Establish a schedule for regular maintenance and inspection of the earthing system and protective devices as per BS 7671 Regulation 651.2. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on proper earthing practices and the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076009 | E20 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted at backside gallery area. ii. Electrical panel exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at backside gallery area. iii. Inadequate cable dressing was observed in most of the distribution boards, with conductors not properly arranged, secured, or terminated neatly. This resulted in untidy wiring, poor segregation between circuits, and unnecessary strain on terminations, which can lead to loose connections, overheating, and difficulty during inspection or fault‑finding. The issue was noted at all distribution boards installed at factory. iv. Phase separators were missing in some panels posing the risk of accidental contact between phases. The issue was noted at ground floor and first floor distribution boards. The utilisation of electrical equipment that is either unsuitable for its operating environment or physically damaged poses significant safety risks. These risks include potential electrical failures, increased likelihood of short circuits, and the heightened risk of fire and electrical shock. | i. Identify and replace electrical panels, cables, and busbars that are not suitable for the environmental conditions in which they are installed in accordance with Section 512.2 of BS 7671 18th Edition + A2 (2022). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076010 | E21 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted at backside gallery area. ii. Electrical panel exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at backside gallery area. iii. Inadequate cable dressing was observed in most of the distribution boards, with conductors not properly arranged, secured, or terminated neatly. This resulted in untidy wiring, poor segregation between circuits, and unnecessary strain on terminations, which can lead to loose connections, overheating, and difficulty during inspection or fault‑finding. The issue was noted at all distribution boards installed at factory. iv. Phase separators were missing in some panels posing the risk of accidental contact between phases. The issue was noted at ground floor and first floor distribution boards. The utilisation of electrical equipment that is either unsuitable for its operating environment or physically damaged poses significant safety risks. These risks include potential electrical failures, increased likelihood of short circuits, and the heightened risk of fire and electrical shock. | ii. Replace or refurbish corroded electrical panels to prevent further degradation and potential safety hazards. Implement protective measures such as installing weatherproof enclosures or using corrosion-resistant materials. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076011 | E22 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted at backside gallery area. ii. Electrical panel exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at backside gallery area. iii. Inadequate cable dressing was observed in most of the distribution boards, with conductors not properly arranged, secured, or terminated neatly. This resulted in untidy wiring, poor segregation between circuits, and unnecessary strain on terminations, which can lead to loose connections, overheating, and difficulty during inspection or fault‑finding. The issue was noted at all distribution boards installed at factory. iv. Phase separators were missing in some panels posing the risk of accidental contact between phases. The issue was noted at ground floor and first floor distribution boards. The utilisation of electrical equipment that is either unsuitable for its operating environment or physically damaged poses significant safety risks. These risks include potential electrical failures, increased likelihood of short circuits, and the heightened risk of fire and electrical shock. | iii. Ensure all distribution boards are properly dressed and organized to prevent mechanical stress on terminals, in accordance with BS 7671:2018+A2:2022. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076012 | E23 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted at backside gallery area. ii. Electrical panel exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at backside gallery area. iii. Inadequate cable dressing was observed in most of the distribution boards, with conductors not properly arranged, secured, or terminated neatly. This resulted in untidy wiring, poor segregation between circuits, and unnecessary strain on terminations, which can lead to loose connections, overheating, and difficulty during inspection or fault‑finding. The issue was noted at all distribution boards installed at factory. iv. Phase separators were missing in some panels posing the risk of accidental contact between phases. The issue was noted at ground floor and first floor distribution boards. The utilisation of electrical equipment that is either unsuitable for its operating environment or physically damaged poses significant safety risks. These risks include potential electrical failures, increased likelihood of short circuits, and the heightened risk of fire and electrical shock. | iv. Install missing phase separators between incoming and outgoing terminations to provide adequate insulation and prevent flashovers between phases, in accordance with BS 7671:2018+A2:2022. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076013 | E24 | DBs & Elec Protection Systems | Panel/cabling/busbar | This relates to the entire facility. The visual site inspection included an examination of the electrical panels, cables and busbars throughout the facility. i. In a number of external areas it was observed that electrical components were not suitable for the environmental conditions in which they were installed. The issue was noted at backside gallery area. ii. Electrical panel exhibited signs of corrosion, indicating potential exposure to moisture or other corrosive elements. The issue was noted at backside gallery area. iii. Inadequate cable dressing was observed in most of the distribution boards, with conductors not properly arranged, secured, or terminated neatly. This resulted in untidy wiring, poor segregation between circuits, and unnecessary strain on terminations, which can lead to loose connections, overheating, and difficulty during inspection or fault‑finding. The issue was noted at all distribution boards installed at factory. iv. Phase separators were missing in some panels posing the risk of accidental contact between phases. The issue was noted at ground floor and first floor distribution boards. The utilisation of electrical equipment that is either unsuitable for its operating environment or physically damaged poses significant safety risks. These risks include potential electrical failures, increased likelihood of short circuits, and the heightened risk of fire and electrical shock. | Establish a schedule for regular maintenance and inspection of the panel, cabling and busbars. Document all inspections and maintenance activities to ensure ongoing compliance. Provide training to facility maintenance personnel on the importance of maintaining electrical safety standards in line with BS 7671 requirements. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076105 | E25 | DBs & Elec Protection Systems | Loop Connection | This relates to the entire facility. During the inspection loop connections were identified within the electrical panels. In these loop connections, one circuit breaker is energised by the live part of another circuit breaker, creating loops within the panel instead of using a busbar system. The issue was noted at LT panel and change over panel at LT room and storage area DB ground floor. Avoiding loop connections is crucial due to several significant risks. Loop connections can complicate maintenance activities, making it difficult to trace and isolate circuits. These connections can lead to increased resistance and overheating, potentially damaging components. Loop connections raise the risk of accidental phase mixing, which can result in short circuits. The above issues compromise personal safety and significantly increase the risk of fire. | All electrical panels shall be modified to eliminate loop connections. A busbar system within the electrical panels shall be utilized to provide each circuit with the required live, neutral, and earth connections. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076102 | E26 | DBs & Elec Protection Systems | Multiple Connections | This relates to the whole facility. During our inspection, multilooping was observed in a number of electrical panels across the facility. In these cases, multiple circuits were being protected by a single circuit breaker. The issue was noted at LT panels, storage area DB ground floor, office DB first floor. Multilooping can result in improper distribution of electrical current, leading to voltage drops and potential electrical hazards. To mitigate these risks and ensure the safety and reliability of the electrical system, it is essential to adhere to proper installation practices. This includes using appropriate dedicated circuit breakers for each circuit. | The electrical installation throughout the facility shall be modified to ensure each circuit is protected by a dedicated circuit breaker of a suitable type and rating for each individual circuit in accordance with Section 430 of BS 7671 18th Edition + A2 (2022). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076003 | E27 | DBs & Elec Protection Systems | Openings | This relates to the entire facility of the factory. During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at electrical room, on-grid solar DB outside main building and busbar DB. These deficiencies pose multiple hazards. Unsealed openings and missing panels expose live electrical components, significantly increasing the risk of accidental contact and electric shock to personnel working nearby. The unsealed openings allow dust, debris, and moisture to enter, which can lead to short circuits and increase the risk of fire. The absence of proper sealing compromises the IP rating of the panels, which is crucial for ensuring safety and protection against environmental factors. | Corrective actions are required to seal all openings and replace missing panels to restore the integrity and safety of the electrical systems. The electrical system shall ensure compliance with Sections 614.2.1, 412.2.2, and 512.2 of BS 7671 18th Edition + A2 (2022). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076004 | E28 | DBs & Elec Protection Systems | Openings | This relates to the entire facility of the factory. During the visual inspection, the electrical panels and distribution boards were examined for unsealed openings to ensure compliance with the IP rating requirements. Unsealed openings were discovered in the panels and distribution boards at electrical room, on-grid solar DB outside main building and busbar DB. These deficiencies pose multiple hazards. Unsealed openings and missing panels expose live electrical components, significantly increasing the risk of accidental contact and electric shock to personnel working nearby. The unsealed openings allow dust, debris, and moisture to enter, which can lead to short circuits and increase the risk of fire. The absence of proper sealing compromises the IP rating of the panels, which is crucial for ensuring safety and protection against environmental factors. | Conduct regular maintenance and maintain comprehensive records for all electrical panels to ensure there are no openings and that the IP ratings of the panels remain uncompromised. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076106 | E29 | DBs & Elec Protection Systems | Adequate accessibility | This relates to the entire facility. During the visit, the electrical panels and distribution boards were examined for adequate accessibility. It was found that the electrical panels are installed at elevated positions and in areas that are not easily accessible, particularly the on-grid solar DB near the busbar panel outside the main building and the solar DBs located at the backside gallery. The excessive mounting height and surrounding obstructions significantly limit safe and convenient access for inspection, maintenance, and emergency intervention. Such restricted accessibility can hinder routine servicing, delay fault diagnosis, and increase response time during electrical emergencies. These conditions may compromise the operational reliability and safety of the electrical system, as proper maintenance and prompt corrective actions are difficult to perform. | Electrical equipment shall be installed with adequate clearances to ensure safe access for inspection, operation, maintenance, and replacement of components, in accordance with Section 132.12 of BS 7671:2018 + A2 (2022). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076006 | E30 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. Lightning strikes can cause significant damage to buildings, primarily through the ignition of fires. When lightning strikes a structure, it can cause an electrical surge that ignites flammable materials. Without a proper lightning protection system (LPS), the energy from a lightning strike can travel through the building's electrical and plumbing systems, creating sparks and starting fires. | Engage a qualified lightning protection specialist to perform a comprehensive risk assessment as per BS EN 62305 (Protection against Lightning). This assessment will determine the necessity of a lightning protection system (LPS) based on factors such as building height, location, occupancy, and the presence of sensitive electronic equipment. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076007 | E31 | DBs & Elec Protection Systems | Lightning Protection System (LPS) | During the inspection, the lightning protection strategy of the factory was assessed. A lightning protection system was provided, however, there was no study available to confirm its adequacy. Lightning strikes can cause significant damage to buildings, primarily through the ignition of fires. When lightning strikes a structure, it can cause an electrical surge that ignites flammable materials. Without a proper lightning protection system (LPS), the energy from a lightning strike can travel through the building's electrical and plumbing systems, creating sparks and starting fires. | If the risk assessment concludes that an LPS is necessary then hire a qualified engineer to perform an adequacy study of the existing LPS. This study should evaluate whether the current system meets the necessary design and performance standards. If the study finds that the current LPS is inadequate, make the necessary upgrades to bring the system up to standard such as BS EN 62305 (Protection against Lightning). | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075990 | E32 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | i. Submit design documentation for the new FADS system to Pakistan Accord for review prior to procurement of any new equipment. Design documentation to include drawings, technical data sheets, and product certifications of all listed equipment to show full compliance with the Fire Alarm and Detection System (FADS) with NFPA 72. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0075991 | E33 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | ii. Submit documentation to the Pakistan Accord showing that an L/C has been opened for import of any components required for the FADS design submitted earlier. | 1 month | 28-Jul-2026 | 27-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0075992 | E34 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | iii. Submit documentation to the Pakistan Accord demonstrating that all materials, both imported and locally procured, have been purchased and are available on-site for installation. | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0075993 | E35 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | iv. Once installation of the FADS system is complete, the factory is to submit full "as-built" documentation of the system to the Pakistan Accord for review. | 5 months | 28-Jul-2026 | 25-Dec-2026 |  |  |  | In progress
Initial inspection | CAP-0075994 | E36 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | v. Factory to advise Pakistan Accord when FADS installation is fully completed and ready for review. Pakistan Accord will then arrange a verification inspection to ensure that the installation fully complies with the previously reviewed design documentation. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0075995 | E37 | Fire Alarm & Detection System (FADS) | Non-functional or incomplete | This section refers to the entire facility. During the inspection, the Fire Alarm and Detection System (FADS) for the facility was evaluated. A conventional fire alarm system was installed at the facility. During the inspection, several deficiencies were noted, including the use of non-addressable and non-listed equipment, inadequate detection coverage, and the use of non-fire-rated cables, all of which pose a significant life-safety risk during a fire emergency. A non-functional or incomplete FADS significantly increases the risk of worker injury or fatality, substantial property damage, operational disruptions, legal liabilities, reputational damage, and environmental harm. A delayed response during a fire event can significantly increase the impact on personnel, goods, and property. | vi. Provide full testing and commissioning (T&C) certification from the FADS system installer and make provision for attendance of the system installer, factory technical personnel, and Pakistan Accord technical team to witness a final T&C demonstration verification on site. On successful completion of this T&C verification inspection, remediation of the FADS system will be complete. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0075996 | E38 | Emergency Lighting | Provided but non-functional | The section refers to the entire facility. During the inspection it was observed that emergency exit sign was provided but not functional at first floor main building. Functional emergency lighting is critical for providing illumination in the event of a power failure or other emergencies, ensuring that workers can safely evacuate the facility. | Conduct a thorough inspection of all emergency exit lights throughout the facility to identify specific locations and units that are non-functional. This includes checking the lights, power sources, batteries, and wiring connections. Repair any faulty emergency exit lights immediately. If repair is not feasible, replace the defective units with new, compliant emergency exit lighting fixtures to ensure adequate illumination for safe evacuation during an emergency. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075997 | E39 | Emergency Lighting | Provided but non-functional | The section refers to the entire facility. During the inspection it was observed that emergency exit sign was provided but not functional at first floor main building. Functional emergency lighting is critical for providing illumination in the event of a power failure or other emergencies, ensuring that workers can safely evacuate the facility. | Establish a regular maintenance and testing schedule to routinely check the functionality of all emergency lights and emergency exit lights. This should include periodic inspections, tests, and prompt corrective actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the proper procedures for inspecting and maintaining emergency lighting and exit systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076000 | E40 | Emergency Lighting | Provided but insufficient | The section refers to the entire facility. During the inspection the emergency lighting arrangement throughout the facility was assessed. The following observations were made: i. Several areas lack sufficient emergency lighting coverage. The issue was noted at stairs, backside gallery area and electrical room. ii. External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations. The issue was noted at assembly area. Adequate and functional emergency lighting throughout the facility is crucial for providing necessary illumination during power failures or other emergencies, ensuring the safe evacuation of workers. | i. Prepare a detailed emergency lighting design based on a comprehensive site survey to identify areas with inadequate coverage, in accordance with the Building Code of Pakistan – Fire Safety Provisions 2016. Submit the proposed emergency lighting layout to Pakistan Accord for review and approval. Upon approval, install additional emergency luminaires in the identified areas to ensure adequate illumination for safe evacuation. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076001 | E41 | Emergency Lighting | Provided but insufficient | The section refers to the entire facility. During the inspection the emergency lighting arrangement throughout the facility was assessed. The following observations were made: i. Several areas lack sufficient emergency lighting coverage. The issue was noted at stairs, backside gallery area and electrical room. ii. External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations. The issue was noted at assembly area. Adequate and functional emergency lighting throughout the facility is crucial for providing necessary illumination during power failures or other emergencies, ensuring the safe evacuation of workers. | ii. Install external emergency luminaires to enable safe evacuation during hours of darkness all the way to a safe place outside the building(s). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076002 | E42 | Emergency Lighting | Provided but insufficient | The section refers to the entire facility. During the inspection the emergency lighting arrangement throughout the facility was assessed. The following observations were made: i. Several areas lack sufficient emergency lighting coverage. The issue was noted at stairs, backside gallery area and electrical room. ii. External emergency lighting was not provided, preventing people from reaching a place of safety outside the facility during nighttime evacuations. The issue was noted at assembly area. Adequate and functional emergency lighting throughout the facility is crucial for providing necessary illumination during power failures or other emergencies, ensuring the safe evacuation of workers. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075998 | E43 | Emergency Lighting | Independent power source | The section refers to the entire facility. During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. Further the emergency lights and exit signs should be reconfigured to be connected on a dedicated single circuit, which must not include any other load except for the emergency lighting system. According to the Building Code of Pakistan Fire Safety Provisions 2016, emergency lighting systems must be designed to provide immediate illumination in the event of power loss to ensure a clear and safe path for evacuation. Ensuring that the emergency lighting is integrated with the facility’s power system to activate automatically during power failures is critical for life safety. This integration helps prevent hazardous conditions that can arise in the dark, such as trips, falls, and confusion, thereby facilitating orderly and efficient evacuation during emergencies. | Reconfigure the emergency lighting circuitry to ensure that emergency lights activate immediately upon failure of general lighting power, and provide an independent circuit for the emergency lighting system, as required by the Building Code of Pakistan Fire Safety Provisions 2016. Submit circuitry design diagrams to Pakistan Accord for review. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075999 | E44 | Emergency Lighting | Independent power source | The section refers to the entire facility. During the inspection, it was observed that the emergency lighting within the facility was not connected in a manner that would ensure automatic activation upon the loss of power to the general lighting in various spaces. Proper circuitry is crucial to ensure that emergency lighting is automatically activated when general lighting fails. This automatic activation is essential for maintaining sufficient illumination, allowing for the safe evacuation of occupants and preventing panic during power outages. Further the emergency lights and exit signs should be reconfigured to be connected on a dedicated single circuit, which must not include any other load except for the emergency lighting system. According to the Building Code of Pakistan Fire Safety Provisions 2016, emergency lighting systems must be designed to provide immediate illumination in the event of power loss to ensure a clear and safe path for evacuation. Ensuring that the emergency lighting is integrated with the facility’s power system to activate automatically during power failures is critical for life safety. This integration helps prevent hazardous conditions that can arise in the dark, such as trips, falls, and confusion, thereby facilitating orderly and efficient evacuation during emergencies. | Establish a regular maintenance and testing schedule to routinely check the functionality of emergency lighting systems. This should include periodic tests, inspections, and prompt maintenance actions to address any issues. Provide independent power circuit to emergency lights. Maintain detailed records of all inspections, tests, repairs, and maintenance activities. Train facility maintenance staff on the procedures for inspecting and maintaining emergency lighting systems to ensure ongoing reliability and compliance with safety standards. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075915 | E45 | Generator, Transformer & Sub-Station Room | Battery | During the inspection of the battery system, the battery cells, connections, and enclosures were thoroughly examined. The battery terminals were exposed and not properly insulated at electrical room, increasing the risk of electrical shock or short circuits. Proper monthly and annual maintenance of the battery system is crucial for fire safety. Spilled fluid can cause corrosion and fires, while bare terminals increase the risk of electrical shocks and short circuits, potentially igniting fires or explosions. Non-compliant battery placement can obstruct ventilation, leading to hazardous gas buildup and fire risks. Addressing these issues is essential to prevent fires and ensure battery system safety. | Insulate exposed battery terminals using appropriate insulating materials to prevent electrical shock and short circuits. Conduct a thorough inspection of all connections to ensure that there are no immediate risks of exposure. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075916 | E46 | Generator, Transformer & Sub-Station Room | Battery | During the inspection of the battery system, the battery cells, connections, and enclosures were thoroughly examined. The battery terminals were exposed and not properly insulated at electrical room, increasing the risk of electrical shock or short circuits. Proper monthly and annual maintenance of the battery system is crucial for fire safety. Spilled fluid can cause corrosion and fires, while bare terminals increase the risk of electrical shocks and short circuits, potentially igniting fires or explosions. Non-compliant battery placement can obstruct ventilation, leading to hazardous gas buildup and fire risks. Addressing these issues is essential to prevent fires and ensure battery system safety. | Establish a routine inspection and maintenance protocol to regularly check and maintain proper insulation of all battery terminals. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075919 | E47 | Cabling & Wiring | Cable support and protection | This section refers to the entire facility. During the inspection of the entire facility, a visual survey of the cable containment system was conducted. Improper or inadequate cable tray/duct support was observed at the stitching area, 1st floor. Weak or incorrectly installed supports compromise the integrity of the containment system, increasing the likelihood of sagging or cable damage. | Ensure all cable trays and ducts are properly supported and structurally sound. Replace or reinforce any weak, unstable, or inadequately mounted systems to maintain cable integrity and system safety. (Reference: BS 7671 18th Edition + A2 (2022), Regulation 522.8.5) | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075920 | E48 | Cabling & Wiring | Cable support and protection | This section refers to the entire facility. During the inspection of the entire facility, a visual survey of the cable containment system was conducted. Improper or inadequate cable tray/duct support was observed at the stitching area, 1st floor. Weak or incorrectly installed supports compromise the integrity of the containment system, increasing the likelihood of sagging or cable damage. | Establish a routine maintenance schedule to assess the condition and support of cable trays. Ensure proper reinforcement and alignment to prevent future sagging or instability. Document findings and corrective actions in maintenance logs. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075925 | E49 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | i. Install cable lugs on all improperly terminated cables within panels and switchgears to secure connections and prevent breaking strands and loose connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022) | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075926 | E50 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | ii. Replace all PVC tape joints with proper terminal blocks or connectors to ensure secure and stable connections in accordance with Regulation 526.1 of BS7671 18th Edition + A2 (2022). Replace all damaged cabling with new wiring. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075929 | E51 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | iii. It is recommended to avoid the use of unsafe plug-in arrangements and ensure that each machine is provided with a properly rated, dedicated socket—preferably of an industrial type. All electrical connections should be carried out in a safe and proper manner in accordance with good engineering practices, as required by BS 7671 (Regs. 553.1.7, 553.2.1, and 134.1.1). | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075927 | E52 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | i. Implement a standard operating procedure (SOP) requiring the use of cable lugs for all future cable terminations. Regularly train and audit personnel to ensure compliance with this procedure, thus maintaining safe and reliable electrical connections. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075928 | E53 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | ii. Establish a policy prohibiting the use of PVC tape for electrical jointing. Regularly inspect and maintain electrical installations to ensure compliance, and provide continuous training for staff on proper jointing techniques. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075930 | E54 | Cabling & Wiring | Splicing of cables | This relates to the whole facility. During the inspection the cable installation was visually surveyed throughout the facility. The following observations were noted: i. Cables terminations within panels and switchgears were made without cable lugs, resulting in breaking strands and loose connections. This presents a significant fire risk due to the potential for electrical arcing and overheating, which can ignite nearby materials and cause a fire. Furthermore, loose connections can cause voltage drops and equipment malfunctions, posing a life safety hazard. The issue was noted at Storage Area DB (Ground Floor) and Office DB (1st Floor). ii. PVC tape joints were found in several locations - including within distribution boards - where cables were either damaged or two cables were being joined together. This method of jointing is unreliable and can deteriorate over time, increasing the risk of electrical shorts and fires. The adhesive on PVC tape can degrade, leading to exposed conductors that can spark and ignite surrounding materials, presenting both fire and life safety risks. The issue was noted at LT Panel, Storage Area DB (Ground Floor), Cable Tray at 1st Floor Stitching Area, and Guard Room. iii. Machine plugs were installed directly into incompatible sockets, creating unsafe electrical connections and increasing the risk of overheating, arcing, and fire. The issue was noted at 1st Floor Stitching Machines. For any future electrical work, the termination of stranded cables must be done with cable lugs and PVC tape joints shall not be utilized. Proper termination ensures secure and reliable connections, reducing the risk of electrical failures and enhancing overall safety. | iii. Conduct regular safety audits and provide training sessions to staff to reinforce the importance of using proper power plugs and adherence to electrical safety standards. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0075921 | E55 | Cabling & Wiring | Colour coding | This relates to the whole facility. During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. The issue was noted at cutting DB ground floor, LT panel and changeover panel at electrical room To mitigate these risks, it is imperative that all future electrical work strictly adheres to standardized colour coding as prescribed by BS 7671. This will ensure accurate identification of conductors, thereby enhancing overall safety and operational efficiency. | Conduct a comprehensive audit of all distribution boards to identify and correct any deviations from the standard cable colour coding. This involves re-labelling or re-insulating the cables with the appropriate colour codes as specified in BS 7671. Specifically, adhere to BS 7671 Regulation 514.3.1, which mandates the correct identification of conductors. | 6 weeks | 28-Jul-2026 | 08-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0075922 | E56 | Cabling & Wiring | Colour coding | This relates to the whole facility. During the inspection of several distribution boards, deviations from standard cable colour coding practices were identified. Such deviations pose significant risks, as they can lead to the misinterpretation and misidentification of cables. This misidentification can result in incorrect connections, potentially causing unsafe working conditions and increasing the likelihood of electrical accidents, such as shocks or fires. The issue was noted at cutting DB ground floor, LT panel and changeover panel at electrical room To mitigate these risks, it is imperative that all future electrical work strictly adheres to standardized colour coding as prescribed by BS 7671. This will ensure accurate identification of conductors, thereby enhancing overall safety and operational efficiency. | Develop and enforce a strict protocol for cable colour coding to be followed in all future installations and maintenance activities. This protocol should include regular training sessions for electricians and maintenance personnel to keep them updated on the latest standards and practices. Additionally, periodic audits should be conducted to ensure ongoing compliance with the standardized colour coding system, thereby preventing future deviations and ensuring sustained safety and operational efficiency. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress

## Fire
Last Inspection Date |  | 17-Mar-2026
Corrective Action Plan - Fire
Factory Name & Address |  | Magna Manufacturing (New Site), 13 Km Daska Road, Sialkot, Punjab, Pakistan
Factory ID |  | 25797
Date of Initial Inspection |  | 17-Mar-2026
Finance Plan Confirmed
INSPECTION TYPE | REFERENCE NUMBER | CAP ITEM NUMBER | CATEGORY | SUBCATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | REMEDIATION START DATE | REMEDIATION END DATE | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
Initial inspection | CAP-0076232 | F1 | Remediation Support | Engineering Support | Some items in the Corrective Action Plan (CAP) will require remediation by a qualified engineer. Please refer to the Remediation Plan for guidance on which tasks can be completed using internal resources and which require engineering support. | Factories should begin remediation of CAP items such as installing extinguishers, signage, and clearing escape routes using internal resources. For fire protection systems, design-related or construction-related remediation, engagement of a qualified Fire Safety Engineer is required. | 8 weeks | 02-Jun-2026 | 28-Jul-2026 |  |  |  | In progress
Initial inspection | CAP-0076245 | F2 | Means of Escape | Escape doors | Per Pakistan Accord Standard, escape doors must meet several requirements so that they can be relied on for escape, the key requirements include: - Doors must not have locking devices regardless of the door is kept locked or unlocked (if a lock is provided, e.g. to prevent unauthorized entry, then it must be overridden by panic hardware). - Doors must have an opening mechanism that allows for easy opening without key or prior knowledge. This is not always achieved, examples include (list not exhaustive): - Most of the escape doors are lockable throughout the facility. Recommended remedial actions are provided below. | Remove all locking devices from doors on all egress routes that could prevent opening from inside. | 2 weeks | 28-Jul-2026 | 11-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0076246 | F3 | Means of Escape | Escape doors | Per Pakistan Accord Standard, escape doors must meet several requirements so that they can be relied on for escape, the key requirements include: - Doors must not have locking devices regardless of the door is kept locked or unlocked (if a lock is provided, e.g. to prevent unauthorized entry, then it must be overridden by panic hardware). - Doors must have an opening mechanism that allows for easy opening without key or prior knowledge. This is not always achieved, examples include (list not exhaustive): - Most of the escape doors are lockable throughout the facility. Recommended remedial actions are provided below. | Escape doors to be side hung doors that open in the direction of escape and provided with easily opening door mechanisms compliant with Accord Building Standard Section 1 Clauses 1.4 and 1.5. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0076247 | F4 | Means of Escape | Escape doors | Per Pakistan Accord Standard, escape doors must meet several requirements so that they can be relied on for escape, the key requirements include: - Doors must not have locking devices regardless of the door is kept locked or unlocked (if a lock is provided, e.g. to prevent unauthorized entry, then it must be overridden by panic hardware). - Doors must have an opening mechanism that allows for easy opening without key or prior knowledge. This is not always achieved, examples include (list not exhaustive): - Most of the escape doors are lockable throughout the facility. Recommended remedial actions are provided below. | Monitor escape door to ensure there are no locking devices installed that prevent easy access to emergency exits. | F3 + 3 months | 26-Oct-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076257 | F5 | Means of Escape | Exit access | Per Pakistan Accord Standard, escape routes within the building should be sufficiently wide and safe for use in an event of an emergency, the key requirements include: - Stairs that discharge inside the building should have routes to the exit that are fire separated from occupancies in the building.. This is not always achieved, examples include (list not exhaustive): - Unprotected openings (windows & exhaust fan) into exit access route at 1st, 2nd & 3rd floor. - Obstructed doors installed in exit routes at 1st, 2nd & 3rd floor (reducing the clear width of escape route). - Stairs discharges inside the building at a distance from building exit i-e S1, S2 and S4. Recommended remedial actions are provided below. | Remove obstructions on escape routes and keep them clear for escape. | 2 weeks | 28-Jul-2026 | 11-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0076258 | F6 | Means of Escape | Exit access | Per Pakistan Accord Standard, escape routes within the building should be sufficiently wide and safe for use in an event of an emergency, the key requirements include: - Stairs that discharge inside the building should have routes to the exit that are fire separated from occupancies in the building.. This is not always achieved, examples include (list not exhaustive): - Unprotected openings (windows & exhaust fan) into exit access route at 1st, 2nd & 3rd floor. - Obstructed doors installed in exit routes at 1st, 2nd & 3rd floor (reducing the clear width of escape route). - Stairs discharges inside the building at a distance from building exit i-e S1, S2 and S4. Recommended remedial actions are provided below. | For stairs discharging within the building, prepare drawings showing the proposed fire separating construction to stair discharge corridor leading outside the building. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge corridors - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks) | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076259 | F7 | Means of Escape | Exit access | Per Pakistan Accord Standard, escape routes within the building should be sufficiently wide and safe for use in an event of an emergency, the key requirements include: - Stairs that discharge inside the building should have routes to the exit that are fire separated from occupancies in the building.. This is not always achieved, examples include (list not exhaustive): - Unprotected openings (windows & exhaust fan) into exit access route at 1st, 2nd & 3rd floor. - Obstructed doors installed in exit routes at 1st, 2nd & 3rd floor (reducing the clear width of escape route). - Stairs discharges inside the building at a distance from building exit i-e S1, S2 and S4. Recommended remedial actions are provided below. | Ensure stair discharge routes / corridors are adequately fire separated from the rest of the building or any fire hazards using 2 hours fire separating construction with 90-minute fire doors. The design shall follow the reviewed proposal and comply with Pakistan Accord Standard. Some of the key requirements include: - All doors into stair discharge corridors need to be fire resisting doors (except stair discharge doors to external air). Penetration through the doors is not permitted. All fire doors require self-closers. Doors into stair discharge routes should be kept closed (but not locked) at all times. - All penetrations through walls into stair discharge corridors need to be fire stopped. Unprotected openings (e.g. holes or window/ louver openings) are not permitted. | F6 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076269 | F8 | Means of Escape | Travel distance | Travel distances should meet the limits in the Pakistan Accord Standard. The standard provides limitations on: - Common path of travel, i.e. the distance the occupants have to travel before there is a choice of escape routes. This is not always achieved, examples include (list not exhaustive): - Common path of travel distances exceed permitted limits and found 28m at 3rd floor. Recommended remedial actions are provided below. | Propose a plan for addressing the excessive travel distance through alternative escape routes and/or additional exits and submit to Pakistan Accord for review prior to commencing any rectification works on site. Review travel distances from all areas in the building(s) to ensure that they meet the limits in the Pakistan Accord Standard. | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076270 | F9 | Means of Escape | Travel distance | Travel distances should meet the limits in the Pakistan Accord Standard. The standard provides limitations on: - Common path of travel, i.e. the distance the occupants have to travel before there is a choice of escape routes. This is not always achieved, examples include (list not exhaustive): - Common path of travel distances exceed permitted limits and found 28m at 3rd floor. Recommended remedial actions are provided below. | Implement the plan previous reviewed by Pakistan Accord and ensure all travel distances to emergency exits meet the requirements of the Pakistan Accord Standard. | F8 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076229 | F10 | Means of Escape | Protection of stairs | Per Pakistan Accord Standard, exit stairs should be adequately protected, including: - Stairs to be fire separated from the rest of the building using 2-hour fire resisting construction with 90-minute fire rated doors. - There should be no fire load and/or services passing through a stair. This is not always achieved, examples include (list not exhaustive): - Missing fire rated enclosure and fire doors in stair S1 , S2 and S4 (all floors). - Fire load under stair S4 (Ground floor). Recommended remedial actions are provided below. | Remove fire load and any other obstructions due to stored items from stairs | 2 weeks | 28-Jul-2026 | 11-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0076230 | F11 | Means of Escape | Protection of stairs | Per Pakistan Accord Standard, exit stairs should be adequately protected, including: - Stairs to be fire separated from the rest of the building using 2-hour fire resisting construction with 90-minute fire rated doors. - There should be no fire load and/or services passing through a stair. This is not always achieved, examples include (list not exhaustive): - Missing fire rated enclosure and fire doors in stair S1 , S2 and S4 (all floors). - Fire load under stair S4 (Ground floor). Recommended remedial actions are provided below. | Prepare drawings showing proposed fire separating construction to protect stairs. These shall be submitted to Pakistan Accord for review and approval prior to rectification works. The drawings should cover: - Layout showing the location of fire rated walls /doors to protect the stairs. - Details of proposed fire resisting walls and fire door assemblies (e.g. fire door listing, fire rating period, self-closers, door opening direction, details of the door opening mechanism and locks). - Location of stair discharge routes and details of fire resisting construction to protect that route. | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076231 | F12 | Means of Escape | Protection of stairs | Per Pakistan Accord Standard, exit stairs should be adequately protected, including: - Stairs to be fire separated from the rest of the building using 2-hour fire resisting construction with 90-minute fire rated doors. - There should be no fire load and/or services passing through a stair. This is not always achieved, examples include (list not exhaustive): - Missing fire rated enclosure and fire doors in stair S1 , S2 and S4 (all floors). - Fire load under stair S4 (Ground floor). Recommended remedial actions are provided below. | Ensure all emergency escape stairs are fire separated from the rest of the building using 2 hours fire separating construction with 90-minute fire doors. The design shall follow Building code of Pakistan Section 10.3.2.1. Key requirements include: - All doors into stairs should be fire resisting doors with self-closing mechanisms. - Penetrations through doors are not permitted. - Doors into stairs should be kept closed (but not locked) at all times. | F11 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076273 | F13 | Means of Escape | Escape stair condition | Per Pakistan Accord Standard, escape stairs should be designed to be safe for use, including day to day use. This is not always achieved, examples include (list not exhaustive): - Missing 1 side handrail in S4. Recommended remedial actions are provided below. | Handrails to be provided on both sides of each stair. Ensure the handrails are at appropriate height. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0076243 | F14 | Means of Escape | Exit discharge | Exit discharge routes outside the building should be sufficiently protected so that people can escape safely in the event of a fire anywhere in the building. This includes: - External escape routes should not lead via unprotected openings. This is not always achieved, examples include (list not exhaustive): - Unprotected openings into external discharge route at south, east & west exit discharge route. Recommended remedial actions are provided below. | Prepare drawings showing proposed fire separating construction to exit discharge routes. These shall be submitted to Accord for review and approval prior to commencing rectification works. The drawings should cover: - Layout showing the location of fire rated walls/doors to protect stair discharge routes - Details of proposed fire resisting walls and fire door assemblies required to protect discharge routes | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076244 | F15 | Means of Escape | Exit discharge | Exit discharge routes outside the building should be sufficiently protected so that people can escape safely in the event of a fire anywhere in the building. This includes: - External escape routes should not lead via unprotected openings. This is not always achieved, examples include (list not exhaustive): - Unprotected openings into external discharge route at south, east & west exit discharge route. Recommended remedial actions are provided below. | - Ensure external exit discharge routes are adequately fire separated from the rest of the building. - Ensure external escape routes do not pass close to unprotected high-risk areas | F14 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076233 | F16 | Means of Escape | Exit signage | Per Pakistan Accord Standard, exits (e.g. escape stairs or final exits leading directly outside the building) must be clearly marked by approved exit signs. Additionally, escape routes leading to these exits need to be signed where the escape route is not readily apparent. The aim of these provisions is for the occupants to be able to easily find and escape route in an event of an emergency. The following deficiencies have been observed on site, including (list not exhaustive): - Missing exit signs at entry into stairs S1, S2 and S4 (all floors). - Missing exit signs at Main Building office area exit door (Ground floor). - Electrically powered exit signs are not a tested and listed system Recommended remedial actions are provided below. | Rectify and/or provide exit signage so access to exits is marked by approved, readily visible signs from all areas of the floor and clearly visible at exits, to comply with Pakistan Accord Standard and BCP 10.15.1, 10.15.2 and 10.15.3 | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0076234 | F17 | Means of Escape | Exit signage | Per Pakistan Accord Standard, exits (e.g. escape stairs or final exits leading directly outside the building) must be clearly marked by approved exit signs. Additionally, escape routes leading to these exits need to be signed where the escape route is not readily apparent. The aim of these provisions is for the occupants to be able to easily find and escape route in an event of an emergency. The following deficiencies have been observed on site, including (list not exhaustive): - Missing exit signs at entry into stairs S1, S2 and S4 (all floors). - Missing exit signs at Main Building office area exit door (Ground floor). - Electrically powered exit signs are not a tested and listed system Recommended remedial actions are provided below. | Ensure that all exit signage is checked periodically and in good working condition. | F16 + 3 months | 26-Oct-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076248 | F18 | Fire Rated Construction | Separation of high-risk areas | Per Pakistan Accord Standard, increased fire risk areas require to be fire separated from the rest of the building using the following: - Electrical rooms, Generator rooms, Fire Pumps room, and Hazardous waste room: 2 hour fire resisting construction with 90 minutes fire doors The following deficiencies have been observed on site, including (list not exhaustive): - Kitchen is not fire separated from the rest of the building at Ground & 1st floor e.g. kitchen not separated from office area at Ground floor. Recommended remedial actions are provided below. | Prepare drawings showing the proposed fire separation details of increased fire hazard areas. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of all increased fire hazard areas in the building (e.g storage, electrical rooms, mechanical rooms, fire pump room etc.) - Locations of fire- rated walls and doors to protect these rooms - Details of proposed fire rated walls and fire doors (e.g. door listing, self-closers, door opening direction) | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076249 | F19 | Fire Rated Construction | Separation of high-risk areas | Per Pakistan Accord Standard, increased fire risk areas require to be fire separated from the rest of the building using the following: - Electrical rooms, Generator rooms, Fire Pumps room, and Hazardous waste room: 2 hour fire resisting construction with 90 minutes fire doors The following deficiencies have been observed on site, including (list not exhaustive): - Kitchen is not fire separated from the rest of the building at Ground & 1st floor e.g. kitchen not separated from office area at Ground floor. Recommended remedial actions are provided below. | Provide 2-hour fire rated construction including 90-minute fire rated doors assemblies according to the layouts and documents reviewed by Pakistan Accord. | F18 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076255 | F20 | Fire Rated Construction | Separation of shafts | Per Pakistan Accord Standard, shafts should be enclosed in 2-hour fire resisting construction to maintain compartmentation between floors. The following deficiencies have been observed on site, including (list not exhaustive): - Proposed lift shaft is not fire separated from rest of the building (all floors). Recommended remedial actions are provided below. | Prepare drawings showing the proposed fire separation details of vertical shafts. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors enclosing vertical shafts. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction) | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076256 | F21 | Fire Rated Construction | Separation of shafts | Per Pakistan Accord Standard, shafts should be enclosed in 2-hour fire resisting construction to maintain compartmentation between floors. The following deficiencies have been observed on site, including (list not exhaustive): - Proposed lift shaft is not fire separated from rest of the building (all floors). Recommended remedial actions are provided below. | Provide 2-hour fire rated protection to lift shafts according to the layouts and documents reviewed by Pakistan Accord. | F20 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076241 | F22 | Fire Rated Construction | Floor openings | Per Pakistan Accord Standard, each floor should be fire separated using 2 hours fire resisting construction with 90 minutes fire rated door/shutter assemblies. The following deficiencies have been observed on site, including (list not exhaustive): - Open voids connecting ground & 1st floor at office area. Recommended remedial actions are provided below. | Prepare a plan and drawings showing the proposed fire separation details. These shall be submitted to the Accord for review and approval prior to the rectification works. The drawings should cover: - Locations of floor openings - Proposed fire separation details (including fire rating of walls and doors) | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076242 | F23 | Fire Rated Construction | Floor openings | Per Pakistan Accord Standard, each floor should be fire separated using 2 hours fire resisting construction with 90 minutes fire rated door/shutter assemblies. The following deficiencies have been observed on site, including (list not exhaustive): - Open voids connecting ground & 1st floor at office area. Recommended remedial actions are provided below. | Provide fire rated separation between floors by implementing the plan reviewed previously by Pakistan Accord. | F22 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076264 | F24 | Fire Rated Construction | Separation of occupancies | Residential sleeping areas should comply with special measures required for sleeping occupancies. Such measures include: - Doors must not have locking devices regardless of the door is kept locked or unlocked (if a lock is provided, e.g. to prevent unauthorized entry, then it must be overridden by panic hardware). - Doors must have an opening mechanism that allows for easy opening without key. - Fire separation of dormitories from other occupancies - Providing a minimum of 2 escape routes from the above ground levels - Providing an automatic fire detection and alarm system - Fire separation of cooking facilities/kitchens from the remainder of the dormitory The following deficiencies have been observed on site at 2nd floor, including (list not exhaustive): - No adequate automatic fire detection and alarm system. - Cooking facilities and/or kitchens not adequately fire separated. - Lack of fire rated separation between the dormitory and other occupancy type. Recommended remedial actions are provided below. | Document proposals for design of remedial measures to ensure compliance with all fire safety requirements for sleeping occupancies to comply with Pakistan Accord Standard. Submit proposals to Pakistan Accord for review. | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076265 | F25 | Fire Rated Construction | Separation of occupancies | Residential sleeping areas should comply with special measures required for sleeping occupancies. Such measures include: - Doors must not have locking devices regardless of the door is kept locked or unlocked (if a lock is provided, e.g. to prevent unauthorized entry, then it must be overridden by panic hardware). - Doors must have an opening mechanism that allows for easy opening without key. - Fire separation of dormitories from other occupancies - Providing a minimum of 2 escape routes from the above ground levels - Providing an automatic fire detection and alarm system - Fire separation of cooking facilities/kitchens from the remainder of the dormitory The following deficiencies have been observed on site at 2nd floor, including (list not exhaustive): - No adequate automatic fire detection and alarm system. - Cooking facilities and/or kitchens not adequately fire separated. - Lack of fire rated separation between the dormitory and other occupancy type. Recommended remedial actions are provided below. | Implement remediation measures to ensure full compliance with dormitory requirements of Pakistan Accord Standard and Pakistan Building Code in accordance with previously reviewed design. | F24 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076260 | F26 | Fire Rated Construction | Storage | Per Pakistan Accord Standard, extensive storage areas need to be fire separated from the rest of the building using 2-hour fire resisting walls with 90 minutes fire rated doors. Limited in-process storage is permitted in production areas, subject to meeting all of the following criteria: - Combined storage areas do not exceed 10% of the production floor area - Storage height is less than 2.45m - Storage areas are grouped into islands not exceeding 23 sq.m. - Islands are separated from other storage islands by at least 3m gap. The following deficiencies have been observed on site, including (list not exhaustive): - Storage areas are not fire separated from the rest of the building e.g. finished goods storage and raw material storage not fire separated from production area at Ground floor and storage at 2nd floor not separated from dinning area. Recommended remedial actions are provided below. | Identify all designated storage areas. Identify which storage areas can be re-arranged to meet the in-process storage limitations described above and which storage areas need will be fire separated from the rest of the building. For all storage areas which require fire separation, prepare a drawing presenting the proposed fire separating construction details and submit to Pakistan Accord for review prior to the rectification works. The drawings should cover: - Locations of fire rated walls and doors. - Details of fire rated walls and fire doors (e.g. listing, fire rating period, self-closers, door opening direction). | 4 months | 28-Jul-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076261 | F27 | Fire Rated Construction | Storage | Per Pakistan Accord Standard, extensive storage areas need to be fire separated from the rest of the building using 2-hour fire resisting walls with 90 minutes fire rated doors. Limited in-process storage is permitted in production areas, subject to meeting all of the following criteria: - Combined storage areas do not exceed 10% of the production floor area - Storage height is less than 2.45m - Storage areas are grouped into islands not exceeding 23 sq.m. - Islands are separated from other storage islands by at least 3m gap. The following deficiencies have been observed on site, including (list not exhaustive): - Storage areas are not fire separated from the rest of the building e.g. finished goods storage and raw material storage not fire separated from production area at Ground floor and storage at 2nd floor not separated from dinning area. Recommended remedial actions are provided below. | Ensure that the above plan is implemented on site following the previously reviewed documentation and in accordance with Pakistan Accord Building Standard. | F26 + 4 months | 25-Nov-2026 | 25-Mar-2027 |  |  |  | In progress
Initial inspection | CAP-0076237 | F28 | Fire Safety Management | Fire drills | Per Pakistan Accord Standard, fire drills shall be conducted as a minimum twice a year. The aim of these drills is to make sure that all staff is adequately trained and suitable provisions are in place to enable timely evacuation in the event of an emergency. The following deficiencies have been observed on site, including (list not exhaustive): - Fire drill documentation is of poor standard (No attendance sheet/visuals attached). -No regular fire drills. Recommended remedial actions are provided below. | Conduct a fire drill and make records, including findings and recommended future improvements. | 2 months | 28-Jul-2026 | 26-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076238 | F29 | Fire Safety Management | Fire drills | Per Pakistan Accord Standard, fire drills shall be conducted as a minimum twice a year. The aim of these drills is to make sure that all staff is adequately trained and suitable provisions are in place to enable timely evacuation in the event of an emergency. The following deficiencies have been observed on site, including (list not exhaustive): - Fire drill documentation is of poor standard (No attendance sheet/visuals attached). -No regular fire drills. Recommended remedial actions are provided below. | Ensure fire drills are performed a minimum of 2 times per year. | F28 + 2 months | 26-Sep-2026 | 25-Nov-2026 |  |  |  | In progress
Initial inspection | CAP-0076235 | F30 | Fire Safety Management | Records of system testing | Per Pakistan Accord Standard, all fire safety systems should be adequately tested to ensure they will operate effectively in an event of an emergency. All fire and life safety systems should be tested in accordance with different standards applicable depending on the system type, e.g. fire suppression systems to NFPA 25, fire alarm and detection system to NFPA 72, fire extinguishers to NFPA 10 etc. The following deficiencies have been observed on site, including (list not exhaustive): - No records of testing of Fire Extinguishers - No records of testing of Emergency Exit Signage Recommended remedial actions are provided below. | - Prepare a schedule of proposed system testing. - Identify how systems will be tested and who is responsible. - The schedule is to be submitted to the Accord for review and approval. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0076236 | F31 | Fire Safety Management | Records of system testing | Per Pakistan Accord Standard, all fire safety systems should be adequately tested to ensure they will operate effectively in an event of an emergency. All fire and life safety systems should be tested in accordance with different standards applicable depending on the system type, e.g. fire suppression systems to NFPA 25, fire alarm and detection system to NFPA 72, fire extinguishers to NFPA 10 etc. The following deficiencies have been observed on site, including (list not exhaustive): - No records of testing of Fire Extinguishers - No records of testing of Emergency Exit Signage Recommended remedial actions are provided below. | #NAME? | F30 + 3 months | 26-Oct-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076271 | F32 | Fire Safety Management | Records of systems maintenance | Per Pakistan Accord Standard, all fire safety systems should be adequately maintained to ensure they will operate effectively in an event of an emergency. All fire and life safety systems should be maintained in accordance with different standards applicable depending on the system type, e.g. fire suppression systems to NFPA 25, fire alarm and detection system to NFPA 72, fire extinguishers to NFPA 10 etc. The following deficiencies have been observed on site, including (list not exhaustive): -No records of maintenance of Fire Extinguishers. -No records of maintenance of Emergency Exit Signage. Recommended remedial actions are provided below. | - Prepare a detailed schedule of proposed system maintenance. Identify who is responsible for filling in the details. - Identify how systems will be maintained and who is responsible. - The schedule is to be submitted to the Accord for review and approval. | 3 months | 28-Jul-2026 | 26-Oct-2026 |  |  |  | In progress
Initial inspection | CAP-0076272 | F33 | Fire Safety Management | Records of systems maintenance | Per Pakistan Accord Standard, all fire safety systems should be adequately maintained to ensure they will operate effectively in an event of an emergency. All fire and life safety systems should be maintained in accordance with different standards applicable depending on the system type, e.g. fire suppression systems to NFPA 25, fire alarm and detection system to NFPA 72, fire extinguishers to NFPA 10 etc. The following deficiencies have been observed on site, including (list not exhaustive): -No records of maintenance of Fire Extinguishers. -No records of maintenance of Emergency Exit Signage. Recommended remedial actions are provided below. | #NAME? | F32 + 3 months | 26-Oct-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076239 | F34 | Fire Safety Management | Emergency Action Plan | Per Pakistan Accord Standard, and Emergency Action Plan shall be developed for each building. The plan shall follow the guidance in NFPA 2800 “Standard on Facility Emergency Action Plans” 2023. Evacuation plans shall be posted at each exit stair and final exit to the outside. Evacuation plans should indicate the location of the plan (i.e. you are here sign), the location of nearby exits, manual call points, and first-aid firefighting provisions. An Emergency Action Plan (EAP) report is required for the site. EAP should describe in detail what should happen in the event of a fire, this includes the roles and responsibilities, training needs, emergency equipment requirements, communication protocols etc. EAP should be practiced as part of evacuation drills. The following deficiencies have been observed on site, including (list not exhaustive): - Escape diagrams are missing on some levels e.g. at 3rd floor. - An EAP document is available; however, It was poor & not as per Pakistan Accord Standard . Recommended remedial actions are provided below. | Ensure that evacuation plans are provided on each level. Prepare an Emergency Action Plan report. | 2 months | 28-Jul-2026 | 26-Sep-2026 |  |  |  | In progress
Initial inspection | CAP-0076240 | F35 | Fire Safety Management | Emergency Action Plan | Per Pakistan Accord Standard, and Emergency Action Plan shall be developed for each building. The plan shall follow the guidance in NFPA 2800 “Standard on Facility Emergency Action Plans” 2023. Evacuation plans shall be posted at each exit stair and final exit to the outside. Evacuation plans should indicate the location of the plan (i.e. you are here sign), the location of nearby exits, manual call points, and first-aid firefighting provisions. An Emergency Action Plan (EAP) report is required for the site. EAP should describe in detail what should happen in the event of a fire, this includes the roles and responsibilities, training needs, emergency equipment requirements, communication protocols etc. EAP should be practiced as part of evacuation drills. The following deficiencies have been observed on site, including (list not exhaustive): - Escape diagrams are missing on some levels e.g. at 3rd floor. - An EAP document is available; however, It was poor & not as per Pakistan Accord Standard . Recommended remedial actions are provided below. | Ensure emergency evacuation plans are provided and up to date. Ensure EAP is being practiced as part of fire drills. | F34 + 2 months | 26-Sep-2026 | 25-Nov-2026 |  |  |  | In progress

## Structural
Last Inspection Date |  | 17-Mar-2026
Corrective Action Plan - Structural
Factory Name & Address |  | Magna Manufacturing (New Site), 13 Km Daska Road, Sialkot, Punjab, Pakistan
Factory ID |  | 25797
Date of Initial Inspection |  | 17-Mar-2026
Finance Plan Confirmed
INSPECTION TYPE | REFERENCE NUMBER | CAP ITEM NUMBER | CATEGORY | SUBCATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | REMEDIATION START DATE | REMEDIATION END DATE | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS
Initial inspection | CAP-0076842 | S1 | Remediation Support | Engineering Support | Some items in the Corrective Action Plan (CAP) will require remediation by a qualified engineer. Please refer to the Remediation Plan for guidance on which tasks can be completed using internal resources and which require engineering support. | Factories should begin remediation of CAP items such as surface cracks or non-structural repairs using internal resources, where available. For remediation based on engineering assessments, detailed engineering assessments, or structural strengthening, engagement of a qualified Structural Engineer is required. | 8 weeks | 02-Jun-2026 | 28-Jul-2026 |  |  |  | In progress
Initial inspection | CAP-0076857 | S2 | Structural System | Connection details | This issue refers to the steel shed at the third floor of the Main Building, where the cross bracing provided for lateral load resistance was observed to be loose, which may compromise the structural stability of the shed. | The cross bracing shall be properly tightened in accordance with the specifications provided in the structural drawings. | 1 month | 28-Jul-2026 | 27-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0076861 | S3 | Other Damage/Defects | Health and Safety | This issue relates to the absence of edge protection on the projection at the first and second floor of the Main Building. This condition presents a potential risk of slip, trip, or fall during service and maintenance, posing a Health & Safety concern. | Provide adequate edge protection on the projection, and on any other part of the factory with the same issue. | 1 month | 28-Jul-2026 | 27-Aug-2026 |  |  |  | In progress
Initial inspection | CAP-0076847 | S4 | Structural Documentation | Documentation unavailable | The approved site layout plan was not available. The first-floor framing plan and relevant details were not available, and no structural details for the lift and stairs were provided in the drawings. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as built documentation. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076863 | S5 | Structural Documentation | Differs from as-built structure | The lift was not shown in the architectural layout plan of the second floor of the Main Building; however, it was observed to be constructed on site. | Building Structural Engineer to carry out on-site survey, collect information and produce accurate and complete as built documentation. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076844 | S6 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the main building. | Building structural engineer to review design documentation to confirm load capacity of the structure. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076845 | S7 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the main building. | Develop safe load plans and submit to Pakistan Accord for review. | 6 months | 28-Jul-2026 | 24-Jan-2027 |  |  |  | In progress
Initial inspection | CAP-0076846 | S8 | Structural Documentation | Lack of safe load plans | No safe load plans posted in the main building. | Factory to post safe load plans on each floor. | S7 + 1 month | 24-Jan-2027 | 23-Feb-2027 |  |  |  | In progress

## Boiler
Last Inspection Date
Corrective Action Plan - Boiler
Factory Name & Address |  | Magna Manufacturing (New Site), 13 Km Daska Road, Sialkot, Punjab, Pakistan
Factory ID |  | 25797
Date of Initial Inspection
Finance Plan Confirmed
INSPECTION TYPE | BOILER INSPECTION TYPE | BOILER NAME | REFERENCE NUMBER | CAP ITEM NUMBER | CATEGORY | SUBCATEGORY | INSPECTION OBSERVATION | REMEDIATION PLAN | TIMING | REMEDIATION START DATE | REMEDIATION END DATE | FACTORY UPDATE | REVISED TIMELINE | INSPECTION COMMENTS | PROGRESS STATUS